## Generalities
FSP 11 59912 - Countis E35/E36/E45/E46 Mbus Tables Indice B
Product name :
Countis E35 : TRI 100 A Mbus / Countis E36 : TRI 100 A Mbus MID
Countis E45 : TRI 5 A Mbus / Countis E46 : TRI 5A Mbus MID
Mbus table version 1.00
Version | 1.03 (D) | Tracability
Application date : | 2013-01-03 | Product | Software version | Communication board version
Issued by : | TMB | Countis E35 : TRI 100 A Mbus | 1.01 | 1.01.01
Division or departement manager : | SCP/DDP/DEV/DLG | Countis E36 : TRI 100 A Mbus MID | 1.01 | 1.01.01
|  | Countis E45 : TRI 5 A Mbus | 1.01 | 1.01.01
|  | Countis E46 : TRI 5A Mbus MID | 1.01 | 1.01.01
Mbus device identification
Description | Value
Device ID | Serial number of the device
Manufacturer ID | "SOC"
Device type | Electricity meter
Legend
Function
3 | Read multiple
6 | Write 1 word
16 | Write multiple

## Telegram description
Telegram description
Telegram 1 : Default telegram
Octets: 69
Description | Unit | Value if not available | M-Bus DIF DataField | M-Bus DIF Function | M-Bus DIF Unit | M-Bus DIF Tariff | M-Bus DIF Storage | M-Bus DIF | M-Bus VIF | M-Bus Value | M-Bus DIF DataField | M-Bus DIF Function | M-Bus DIF Unit | M-Bus DIF Tariff | M-Bus DIF Storage | M-Bus DIF | M-Bus VIF | M-Bus Value | M-Bus DIF DataField | M-Bus DIF Function | M-Bus DIF Unit | M-Bus DIF Tariff | M-Bus DIF Storage | M-Bus DIF | M-Bus VIF | M-Bus Value | M-Bus DIF DataField | M-Bus DIF Function | M-Bus DIF Unit | M-Bus DIF Tariff | M-Bus DIF Storage | M-Bus DIF | M-Bus VIF | M-Bus Value | M-Bus DIF DataField | M-Bus DIF Function | M-Bus DIF Unit | M-Bus DIF Tariff | M-Bus DIF Storage
Total Positive Active Energy (no resetable) : Ea+ | kWh | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0x06 (kWh) | 32 bit signed integer
Total Positive Reactive Energy (no resetable) : Er + | kvarh | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 01 = Storage 1 | 0x44 | 0xFB 0x02 (kVARh) | 32 bit signed integer
Total Negative Active Energy (no resetable) : Ea- | kWh | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 02 = Storage 2 | 0x84 0x01 | 0x06 (kWh) | 32 bit signed integer
Tariff number in progress ( 1 to 4 ) |  | 0 | 02 = Signed Integer 2 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x02 | 0x7C 0x03 0x72 0x61 0x74 (text "tar") | 16 bit signed integer
4 * Positive Active Energies | kWh | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 0A = Storage 10 | 0x84 0x05 | 0x06 (kWh) | 32 bit signed integer | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 0B = Storage 11 | 0xC4 0x05 | 0x06 (kWh) | 32 bit signed integer | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 0C = Storage 12 | 0x84 0x06 | 0x06 (kWh) | 32 bit signed integer | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 0D = Storage 13 | 0xC4 0x06 | 0x06 (kWh) | 32 bit signed integer | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 0E = Storage 14
4 * Positive Reactive Enegies | kvarh | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 14 = Storage 20 | 0x84 0x0A | 0xFB 0x02 (kVARh) | 32 bit signed integer | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 15 = Storage 21 | 0xC4 0x0A | 0xFB 02 (kVARh) | 32 bit signed integer | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 16 = Storage 22 | 0x84 0x0B | 0xFB 02 (kVARh) | 32 bit signed integer | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 17 = Storage 23 | 0xC4 0x0B | 0xFB 02 (kVARh) | 32 bit signed integer | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 18 = Storage 24
∑ Active Power +/- : P | kW/100 (Signed) | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0x2C (10 W) | 32 bit signed integer
Active Power phase 1 +/- : P1 | kW/100 (Signed) | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xAC 0xFC 0x01 (10 W at phase 1) | 32 bit signed integer
Active Power phase 2 +/- : P2 | kW/100 (Signed) | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xAC 0xFC 0x02 (10 W at phase 2) | 32 bit signed integer
Active Power phase 3 +/- : P3 | kW/100 (Signed) | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xAC 0xFC 0x03 (10 W at phase 3) | 32 bit signed integer
Current Transformer primary | A | 0x7FFF | 02 = Signed Integer 2 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 02 = Storage 2 | 0x82 0x01 | 0xFD 0x67 (Special Supplier Info) | 16 bit signed integer
Phase to Phase Voltage: U12 | V/100 | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xFD 0xC7 0xFC 0x05 (10 mV between phase 1 and 2) | 32 bit signed integer
Phase to Phase Voltage: U23 | V/100 | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xFD 0xC7 0xFC 0x06 (10 mV between phase 2 and 3) | 32 bit signed integer
Phase to Phase Voltage: U31 | V/100 | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xFD 0xC7 0xFC 0x07 (10 mV between phase 3 and 1) | 32 bit signed integer
Simple voltage : V1 | V/100 | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xFD 0xC7 0xFC 0x01 (10 mV at phase 1) | 32 bit signed integer
Simple voltage : V2 | V/100 | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xFD 0xC7 0xFC 0x02 (10 mV at phase 2) | 32 bit signed integer
Simple voltage : V3 | V/100 | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xFD 0xC7 0xFC 0x03 (10 mV at phase 3) | 32 bit signed integer
Current : I1 | mA | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xFD 0xD9 0xFC 0x01 (mA at phase 1) | 32 bit signed integer
Current : I2 | mA | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xFD 0xD9 0xFC 0x02 (mA at phase 2) | 32 bit signed integer
Current : I3 | mA | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xFD 0xD9 0xFC 0x03 (mA at phase 3) | 32 bit signed integer
Neutral Current : In | mA | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xFD 0x59 (mA) | 32 bit signed integer
Telegram 2 : Energies
Octets: 69
Description | Unit | Value if not available | M-Bus DIF DataField | M-Bus DIF Function | M-Bus DIF Unit | M-Bus DIF Tariff | M-Bus DIF Storage | M-Bus DIF | M-Bus VIF | M-Bus Value | M-Bus DIF DataField | M-Bus DIF Function | M-Bus DIF Unit | M-Bus DIF Tariff | M-Bus DIF Storage | M-Bus DIF | M-Bus VIF | M-Bus Value | M-Bus DIF DataField | M-Bus DIF Function | M-Bus DIF Unit | M-Bus DIF Tariff | M-Bus DIF Storage | M-Bus DIF | M-Bus VIF | M-Bus Value | M-Bus DIF DataField | M-Bus DIF Function | M-Bus DIF Unit | M-Bus DIF Tariff | M-Bus DIF Storage | M-Bus DIF | M-Bus VIF | M-Bus Value | M-Bus DIF DataField | M-Bus DIF Function | M-Bus DIF Unit | M-Bus DIF Tariff | M-Bus DIF Storage
Total Positive Active Energy (no resetable) : Ea+ | kWh | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0x06 (kWh) | 32 bit signed integer
Total Positive Reactive Energy (no resetable) : Er + | kvarh | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 01 = Storage 1 | 0x44 | 0xFB 0x02 (kVARh) | 32 bit signed integer
Total Negative Active Energy (no resetable) : Ea- | kWh | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 02 = Storage 2 | 0x84 0x01 | 0x06 (kWh) | 32 bit signed integer
Partial Positive Active Energy: Ea+ | kWh | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 03 = Storage 3 | 0xC4 0x01 | 0x06 (kWh) | 32 bit signed integer
Partial Positive Reactive Energy: Er + | kvarh | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 04 = Storage 4 | 0x84 0x02 | 0xFB 0x02 (kVARh) | 32 bit signed integer
Partial Negative Active Energy : Ea- | kWh | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 05 = Storage 5 | 0xC4 0x02 | 0x06 (kWh) | 32 bit signed integer
Tariff number in progress ( 1 to 4 ) |  | 0 | 02 = Signed Integer 2 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x02 | 0x7C 0x03 0x72 0x61 0x74 (text "tar") | 16 bit signed integer
4 * Positive Active Energies | kWh | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 0A = Storage 10 | 0x84 0x05 | 0x06 (kWh) | 32 bit signed integer | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 0B = Storage 11 | 0xC4 0x05 | 0x06 (kWh) | 32 bit signed integer | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 0C = Storage 12 | 0x84 0x06 | 0x06 (kWh) | 32 bit signed integer | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 0D = Storage 13 | 0xC4 0x06 | 0x06 (kWh) | 32 bit signed integer | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 0E = Storage 14
4 * Positive Reactive Enegies | kvarh | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 14 = Storage 20 | 0x84 0x0A | 0xFB 0x02 (kVARh) | 32 bit signed integer | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 15 = Storage 21 | 0xC4 0x0A | 0xFB 02 (kVARh) | 32 bit signed integer | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 16 = Storage 22 | 0x84 0x0B | 0xFB 02 (kVARh) | 32 bit signed integer | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 17 = Storage 23 | 0xC4 0x0B | 0xFB 02 (kVARh) | 32 bit signed integer | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 18 = Storage 24
Telegram 3 : Metrology
Octets: 88
Description | Unit | Value if not available | M-Bus DIF DataField | M-Bus DIF Function | M-Bus DIF Unit | M-Bus DIF Tariff | M-Bus DIF Storage | M-Bus DIF | M-Bus VIF | M-Bus Value
Phase to Phase Voltage: U12 | V/100 | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xFD 0xC7 0xFC 0x05 (10 mV between phase 1 and 2) | 32 bit signed integer
Phase to Phase Voltage: U23 | V/100 | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xFD 0xC7 0xFC 0x06 (10 mV between phase 2 and 3) | 32 bit signed integer
Phase to Phase Voltage: U31 | V/100 | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xFD 0xC7 0xFC 0x07 (10 mV between phase 3 and 1) | 32 bit signed integer
Simple voltage : V1 | V/100 | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xFD 0xC7 0xFC 0x01 (10 mV at phase 1) | 32 bit signed integer
Simple voltage : V2 | V/100 | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xFD 0xC7 0xFC 0x02 (10 mV at phase 2) | 32 bit signed integer
Simple voltage : V3 | V/100 | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xFD 0xC7 0xFC 0x03 (10 mV at phase 3) | 32 bit signed integer
Current : I1 | mA | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xFD 0xD9 0xFC 0x01 (mA at phase 1) | 32 bit signed integer
Current : I2 | mA | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xFD 0xD9 0xFC 0x02 (mA at phase 2) | 32 bit signed integer
Current : I3 | mA | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xFD 0xD9 0xFC 0x03 (mA at phase 3) | 32 bit signed integer
Neutral Current : In | mA | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xFD 0x59 (mA) | 32 bit signed integer
Telegram 4 : Powers
Bytes: 147
Description | Unit | Value if not available | M-Bus DIF DataField | M-Bus DIF Function | M-Bus DIF Unit | M-Bus DIF Tariff | M-Bus DIF Storage | M-Bus DIF | M-Bus VIF | M-Bus Value
∑ Active Power +/- : P | kW/100 (Signed) | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0x2C (10 W) | 32 bit signed integer
∑ Reactive Power +/- : Q | kvar/100 (Signed) | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xFB 0x15 (10 VAR) | 32 bit signed integer
∑ Apparent Power : S | kVA/100 | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0x2C (10 W) | 32 bit signed integer
∑ Power Factor : -: leading et + : lagging : PF | 0,001 (Signed) | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xFD 0xBA 0x73 (No VIF * 10e-3) | 32 bit signed integer
Active Power phase 1 +/- : P1 | kW/100 (Signed) | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xAC 0xFC 0x01 (10 W at phase 1) | 32 bit signed integer
Active Power phase 2 +/- : P2 | kW/100 (Signed) | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xAC 0xFC 0x02 (10 W at phase 2) | 32 bit signed integer
Active Power phase 3 +/- : P3 | kW/100 (Signed) | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xAC 0xFC 0x03 (10 W at phase 3) | 32 bit signed integer
Reactive Power phase 1 +/- : Q1 | kvar/100 (Signed) | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xFB 0x95 0xFC 0x01 (10 VAR at phase 1) | 32 bit signed integer
Reactive Power phase 2 +/- : Q2 | kvar/100 (Signed) | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xFB 0x95 0xFC 0x02 (10 VAR at phase 2) | 32 bit signed integer
Reactive Power phase 3 +/- : Q3 | kvar/100 (Signed) | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xFB 0x95 0xFC 0x03 (10 VAR at phase 3) | 32 bit signed integer
Apparent Power phase 1 : S1 | kVA/100 | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xFC 0xF4 0xFC 0x01 0x03 0x41 0x56 0x6b (text "kVA" * 10e-2 at phase 1) | 32 bit signed integer
Apparent Power phase 2 : S2 | kVA/100 | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xFC 0xF4 0xFC 0x02 0x03 0x41 0x56 0x6b (text "kVA" * 10e-2 at phase 2) | 32 bit signed integer
Apparent Power phase 3 : S3 | kVA/100 | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xFC 0xF4 0xFC 0x03 0x03 0x41 0x56 0x6b (text "kVA" * 10e-2 at phase 3) | 32 bit signed integer
Power Factor phase 1 -: leading and + : lagging : PF1 | 0,001 (Signed) | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xFD 0xBA 0xF3 0xFC 0x01 (No VIF * 10e-3 at phase 1) | 32 bit signed integer
Power Factor phase 2 -: leading and + : lagging : PF2 | 0,001 (Signed) | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xFD 0xBA 0xF3 0xFC 0x02 (No VIF * 10e-3 at phase 2) | 32 bit signed integer
Power Factor phase 3 -: leading and + : lagging : PF3 | 0,001 (Signed) | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xFD 0xBA 0xF3 0xFC 0x03 (No VIF * 10e-3 at phase 3) | 32 bit signed integer
Telegram 5 : History
Bytes: 94
Description | Unit | Value if not available | M-Bus DIF DataField | M-Bus DIF Function | M-Bus DIF Unit | M-Bus DIF Tariff | M-Bus DIF Storage | M-Bus DIF | M-Bus VIF | M-Bus Value
Ea + for day n-1 | kWh | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 1E = Storage 30 | 0x84 0x0F | 0x06 (kWh) | 32 bit signed integer
Ea - for day n-1 | kWh | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 20 = Storage 32 | 0x84 0x80 0x01 | 0x06 (kWh) | 32 bit signed integer
Ea + for day n | kWh | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 1F = Storage 31 | 0xC4 0x0F | 0x06 (kWh) | 32 bit signed integer
Ea - for day n | kWh | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 21 = Storage 33 | 0xC4 0x80 0x01 | 0x06 (kWh) | 32 bit signed integer
Ea + for Week n-1 | kWh | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 28 = Storage 40 | 0x84 0x84 0x01 | 0x06 (kWh) | 32 bit signed integer
Ea - for Week n-1 | kWh | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 2A = Storage 42 | 0x84 0x85 0x01 | 0x06 (kWh) | 32 bit signed integer
Ea + for Week n | kWh | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 29 = Storage 41 | 0xC4 0x84 0x01 | 0x06 (kWh) | 32 bit signed integer
Ea - for Week n | kWh | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 2B = Storage 43 | 0xC4 0x85 0x01 | 0x06 (kWh) | 32 bit signed integer
Ea + for Month n-1 | kWh | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 32 = Storage 50 | 0x84 0x89 0x01 | 0x06 (kWh) | 32 bit signed integer
Ea - for Month n-1 | kWh | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 34 = Storage 52 | 0x84 0x8A 0x01 | 0x06 (kWh) | 32 bit signed integer
Ea + for Month n | kWh | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 33 = Storage 51 | 0xC4 0x89 0x01 | 0x06 (kWh) | 32 bit signed integer
Ea - for Month n | kWh | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 35 = Storage 53 | 0xC4 0x8A 0x01 | 0x06 (kWh) | 32 bit signed integer
Telegram 6 : Advanced information
Bytes: 80
Description | Unit | Value if not available | M-Bus DIF DataField | M-Bus DIF Function | M-Bus DIF Unit | M-Bus DIF Tariff | M-Bus DIF Storage | M-Bus DIF | M-Bus VIF | M-Bus Value
Product order ID (Countis:100, Protection:200, Atys:300, Diris:400) |  | 0x7FFF | 02 = Signed Integer 2 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x02 | 0xFD 0x0C (Model / Version) | 16 bit signed integer
Product ID (EX: 1000 ATS3) |  | 0x7FFF | 02 = Signed Integer 2 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 01 = Storage 1 | 0x42 | 0xFD 0x0C (Model / Version) | 16 bit signed integer
Product software version (EX: 100 Version 1.00) |  | 0x7FFF | 02 = Signed Integer 2 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x02 | 0xFD 0x0F (Software Version #) | 16 bit signed integer
Serial_AA_SS | Poids fort : AA poids faible : SS | 0x7FFF | 02 = Signed Integer 2 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 01 = Storage 1 | 0x42 | 0x79 (Enhanced Identification) | 16 bit signed integer
Serial_SST_L | Poids fort : SST poids faible : L | 0x7FFF | 02 = Signed Integer 2 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 02 = Storage 2 | 0x82 0x01 | 0x79 (Enhanced Identification) | 16 bit signed integer
Serial_order |  | 0x7FFF | 02 = Signed Integer 2 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 03 = Storage 3 | 0xC2 0x01 | 0x79 (Enhanced Identification) | 16 bit signed integer
Serial_Reserve |  | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 04 = Storage 4 | 0x84 0x02 | 0x79 (Enhanced Identification) | 16 bit signed integer
Network Type : 0 : 1BL 1 : 2BL 2 : 3BL 3 : 3NBL 4 : 4BL 5 : 4NBL | – | 0x7FFF | 02 = Signed Integer 2 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x02 | 0xFD 0x67 (Special Supplier Info) | 16 bit signed integer
Current Transformer secondary : 1: 1 A 5: 5 A | A | 0x7FFF | 02 = Signed Integer 2 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 01 = Storage 1 | 0x42 | 0xFD 0x67 (Special Supplier Info) | 16 bit signed integer
Current Transformer primary | A | 0x7FFF | 02 = Signed Integer 2 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 02 = Storage 2 | 0x82 0x01 | 0xFD 0x67 (Special Supplier Info) | 16 bit signed integer
Synchronisation Top for P+/- Q+/- : time in seconds ( 1mn, 5mn, 8mn, 10mn, 15mn, 20mn, 30mn, 60mn) | secondes | 0x7FFF | 02 = Signed Integer 2 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 03 = Storage 3 | 0xC2 0x01 | 0xFD 0x67 (Special Supplier Info) | 16 bit signed integer
Day |  | 0x7FFF | 06 = Signed Integer 6 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x06 | 0x6D (Date + Time) | 48 Bit Date + Time Type I
Month |  | 0x7FFF
Year |  | 0x7FFF
Hour |  | 0x7FFF
Minute |  | 0x7FFF
Second |  | 0x7FFF
Tariff number in progress ( 1 to 8 ) |  | 0 | 02 = Signed Integer 2 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x02 | 0x7C 0x03 0x72 0x61 0x74 ("tar") | 16 bit signed integer
Telegram 7 : Load curves instantaneous
Bytes: 11
Description | Unit | Value if not available | M-Bus DIF DataField | M-Bus DIF Function | M-Bus DIF Unit | M-Bus DIF Tariff | M-Bus DIF Storage | M-Bus DIF | M-Bus VIF | M-Bus Value
Last date for Record average P/Q/S in second since 01/01/2000 | s | 0x7FFFFFFF | 04 = Signed Integer 4 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x04 | 0xFD 0x2C (Duration since last Readout [s]) | 32 bit signed integer
Last average (P+) | 10W ( no affected by CT and VT ) | 0x7FFF | 02 = Signed Integer 2 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 00 = Storage 0 | 0x02 | 0x2C (10 W) | 16 bit signed integer
Telegram 8 : Load curves / First data packet
Bytes: 204
Description | Unit | Value if not available | M-Bus DIF DataField | M-Bus DIF Function | M-Bus DIF Unit | M-Bus DIF Tariff | M-Bus DIF Storage | M-Bus DIF | M-Bus VIF | M-Bus Value
Record count ( Maximum 24 ) |  | 0x7FFF | 0F = Special function | 01 = More records following |  |  |  | 0x0F | No VIF | 204 bytes data
Record size = 4 see below the data record description | Nb Words | 0x7FFF |  | 00 = Last records
Integration period | second | 0x7FFF
Type Information 0 : P+(w) 1 : P-(w) 2 : Q+(VAr) 3 : Q-(VAr) 4 : S ( VA) 5 : Tang Phi 6 : Eau(m3) 7 : Gaz 8 : Air 9 : Imp | Base Unit P+ : w P- : w Q+ : VAr Q- : VAr S : VA Tang Phi : None Eau : m3 Gaz : None Air : None Impuls : None | 0x7FFF
Numerator Rate |  | 0x7FFF
Denominator Rate |  | 0x7FFF
Records (x24) see below the description |  | 0x7FFF | not defined | not defined | not defined | not defined | not defined
Word Count | Description | Unit
2 | Date | second since 1st jan 2000
1 | Full/incomplete period | 0 : full integration period 1 : incomplete integration period
1 | Value without CT*VT rate | Unit = Base Unit * Numerator Rate / Denominator Rate
Telegram 9 : Indus Mode
Bytes: 6
Description | Unit | Value if not available | M-Bus DIF DataField | M-Bus DIF Function | M-Bus DIF Unit | M-Bus DIF Tariff | M-Bus DIF Storage | M-Bus DIF | M-Bus VIF | M-Bus Value
Indus Mode |  | 0x7FFF | 02 = Signed Integer 2 Bytes | 00 = Instantaneous | 00 = Unit 0 | 00 = Tariff 0 | 04 = Storage 4 | 0xC2 0x02 | 0xFD 0x67 (Special Supplier Info) | 16 bit signed integer

## Command description
Commands to send from Master to Slave to configure a slave (Countis)
The commands are sent using SND_UD
Command | Description | CI Field | DIB | VIB | DATA
Set Date/Time | Set Date and Time of the meter | 0x51 | 0x06 | 0x6D | 6 bytes(1) | (1) Coding of date and time
Select Telegram | Set the telegram to send in answer to an REQ_UD2 command. See "Telegram description" to know the content of each telegram. Valid values are 1xh with x=Telegram number (1 to 8) | 0x50 | No DIF | No VIF | 1 byte
Com. Board Processor RESET | Software Reset of the communication board (like power off - power on) | 0x50 | No DIF | No VIF | 1 byte=0x90 |  | Byte/bit | msb | [6 empty] | lsb
Set baud rate to 300bps | Change the communication baud rate. A valid message must be sent in the 2 minutes after this command in order to confirm the new baud rate. If the countis is in Auto Baud mode, it will switch in manual mode. | 0xB8 | No DIF | No VIF | No Data |  | lsB | 0 | 0 | seconds | seconds | seconds | seconds | seconds | seconds | seconds: 0 to 59
Set baud rate to 600bps |  | 0xB9 | No DIF | No VIF | No Data |  |  | 0 | 0 | minutes | minutes | minutes | minutes | minutes | minutes | minutes: 0 to 59
Set baud rate to 1200bps |  | 0xBA | No DIF | No VIF | No Data |  |  | 0 | 0 | 0 | hour | hour | hour | hour | hour | hour: 0 to 23
Set baud rate to 2400bps |  | 0xBB | No DIF | No VIF | No Data |  |  | year(b2) | year(b1) | year(b0) | day | day | day | day | day | day: 1 to 31
Set baud rate to 4800bps |  | 0xBC | No DIF | No VIF | No Data |  |  | year(b6) | year(b5) | year(b4) | year(b3) | month | month | month | month | month: 1 to 12
Set baud rate to 9600bps |  | 0xBD | No DIF | No VIF | No Data |  | msB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | year: 0 to 99 since 2000
Set baud rate to 19200bps | These baud rates are not supported, in this case the countis switch to Auto Baud. | 0xBE | No DIF | No VIF | No Data
Set baud rate to 38400bps |  | 0xBF | No DIF | No VIF | No Data |  | Example : | 03 avril 2012 14h30min30s : 0x1E 0x1E 0x0E 0x83 0x14 0x00
Set primary address (0-250) | Set the primary address of the countis. Valid values are in the range 0-250. Address 0 is reserved for first installation and is the default value after manufacturing. | 0x51 | 0x01 | 0x7A | 1 byte
Set secondary address (Manufacturer ID) | Set the Manufacturer Id for secondary addressing of the countis. Valid values are in the range 00000000-99999999. This Id is unique for the manufacturer and should not be changed. | 0x51 | 0x0C | 0x79 | 8 BCD (4 bytes) | (2) Full Address
Set secondary address (Full address) | Set the Manufacturer Id, Manufacturer code, Generation and Medium codes for secondary addressing of the countis. These codes form a unique address and should not be changed. | 0x51 | 0x07 | 0x79 | 64 bits(2) |  |  | Manufacturer ID |  | Manufacturer Code |  | Generation |  | Medium
Set current tariff (1-4) | Set the current tariff | 0x51 | 0x02 | 0x7C 0x03 0x72 0x61 0x74 | 1 Word |  |  |  |  | (not changeable) |  |  |  | (not changeable)
Reset Pmax | Reinitialize the Max power record | 0x51 | 0x14 | 0xAC 0x07 | No data |  |  | 8 BCD (4 bytes) |  | E3h 4Dh |  | 1 byte |  | 1 byte=03h
Reset Partial energies | Reinitialize partial energies | 0x51 | 0xC4 0x01 | 0x86 0x07 | No data
Set Network | Set the network configuration | 0x51 | 0x02 | 0xFD 0x67 | 1 Word(3) | Data are coded LSB first.
Set Secondary CT | Set the Secondary curent transformer ratio | 0x51 | 0x42 | 0xFD 0x67 | 1 Word(4)
Set Primary CT | Set the Primary curent transformer ratio | 0x51 | 0x82 0x01 | 0xFD 0x67 | 1 Word | Example:
Set Integration Time | Set the integration time in minutes (load curve) (1, 5, 8, 10, 15, 20, 30, 60) | 0x51 | 0xC2 0x01 | 0xFD 0x67 | 1 Word | Man. ID= 12345678, Man. Code=4Dh E3h, Generation=4; Medium=3
78h, 56h, 34h, 12h, E3h, 4Dh, 04h, 03h
(3) Network
0=1BL
1=2BL
2=3BL
3=3NBL
4=4BL
5=4NBL
(4) Set Secondary CT
1= TC1A
5=TC5A

## Special informations Load curve
Load curve telegrams are a set of telegrams with a manufacturer specific format. The first record sent is the last saved (the more recent). After receiving the command to switch to this telegram (SND_UD with CI field=0x50 and data=0x17) , the countis restart the telegram sending to the begining. A complete load curve is composed of 42 telegrams of 24 records each, 1008 records in total.
The user datafield of one telegram is composed as folowing:
Description | Size | Value | Comments
DIF | 1 Byte | 0x0F or 0x1F | 0F if there's a folowing telegram, 1F if it's the last
Record count | 1 Word | 24 maxi | Number of records in the telegram
Record Size | 1 Word | 4 | Number od words per record
Integration period | 1 Word |  | Integration period in seconds
Information type | 1 Word | 0 | P+ (W)
Numerator rate | 1 Word
Denominator rate | 1 Word
Date | 2 Words |  | Seconds since Jan 2000 | x 24
Full/Incomplete period | 1 Word | 0 or 1 | 0 : full integration period 1 : incomplete integration period
Value without CT*VT rate | 1 Word |  | Unit = Base Unit * Numerator Rate / Denominator Rate
The power value in Watt = Value x Numerator / Denominator

## Frame description
Single Character | Short Frame | Control Frame | Long Frame
E5h | Start 10h | Start 68h | Start 68h
| C Field | L Field = 3 | L Field
| A Field | L Field = 3 | L Field
| Check Sum | Start 68h | Start 68h
| Stop 16h | C Field | C Field
|  | A Field | A Field
|  | CI Field | CI Field
|  | Check Sum | User Data
|  | Stop 16h | (0-252 Byte)
Check Sum
Stop 16h
Single Character
This format consists of a single character, namely the E5h (decimal 229), and serves to acknowledge receipt of transmissions.
Short Frame
This format with a fixed length begins with the start character 10h, and besides the C and A fields includes the check sum (this is made up from the two last mentioned characters), and the stop character 16h.
Long Frame
With the long frame, after the start character 68h, the length field (L field) is first transmitted twice, followed by the start character once again. After this, there follow the function field (C field), the address field (A field) and the control information field (CI field). The L field gives the quantity of the user data inputs plus 3 (for C,A,CI). After the user data inputs, the check sum is transmitted, which is built up over the same area as the length field, and in conclusion the stop character 16h is transmitted.
Control Frame
The control sentence conforms to the long sentence without user data, with an L field from the contents of 3. The check sum is calculated at this point from the fields C, A and CI.
For a complete description of each field, refer to EN 13757-2