## Sheet1
SOCOMEC PRODUCTS: |  |  |  | 1.3.6.1.4.1.4555.10
| PRODUCT IDENTIFICATION |  |  |  | 1.3.6.1.4.1.4555.10.10
|  |  | MODBUS ADDRESS |  |  |  | 1.3.6.1.4.1.4555.10.10.10.1.1
|  |  | OPERATING HOURS COUNTER |  |  |  | 1.3.6.1.4.1.4555.10.10.10.1.65535
The DIRIS Digiware D-70 is a Modbus to SNMP gateway. The final OID for a parameter uses the Modbus address and Load # of a PMD.
| MEASUREMENTS |  |  |  | 1.3.6.1.4.1.4555.10.20 |  |  | Unit | Function
|  | ENERGIES |  |  |  | 1.3.6.1.4.1.4555.10.20.12
|  |  | TOTAL POSITIVE ACTIVE ENERGY (+) |  |  |  | 1.3.6.1.4.1.4555.10.20.12.1.30000 | kWh | Read
|  |  | TOTAL RESIDUAL ACTIVE ENERGY (+) |  |  |  | 1.3.6.1.4.1.4555.10.20.12.1.30001 | (1/10) Wh | Read
|  |  | TOTAL ACTIVE ENERGY (-) |  |  |  | 1.3.6.1.4.1.4555.10.20.12.1.30002 | kWh | Read
|  |  | TOTAL RESIDUAL ACTIVE ENERGY (-) |  |  |  | 1.3.6.1.4.1.4555.10.20.12.1.30003 | (1/10) Wh | Read
|  |  | TOTAL REACTIVE ENERGY (+) |  |  |  | 1.3.6.1.4.1.4555.10.20.12.1.30004 | kVarh | Read
|  |  | TOTAL RESIDUAL REACTIVE ENERGY (+) |  |  |  | 1.3.6.1.4.1.4555.10.20.12.1.30005 | (1/10) Varh | Read
|  |  | TOTAL REACTIVE ENERGY (-) |  |  |  | 1.3.6.1.4.1.4555.10.20.12.1.30006 | kVarh | Read
|  |  | TOTAL RESIDUAL REACTIVE ENERGY (-) |  |  |  | 1.3.6.1.4.1.4555.10.20.12.1.30007 | (1/10) Varh | Read
|  |  | TOTAL APPARENT ENERGY |  |  |  | 1.3.6.1.4.1.4555.10.20.12.1.30016 | kVAh | Read
|  |  | TOTAL RESIDUAL APPARENT ENERGY |  |  |  | 1.3.6.1.4.1.4555.10.20.12.1.30017 | (1/10) Vah | Read
|  |  | PARTIAL POSITIVE ACTIVE ENERGY (+) |  |  |  | 1.3.6.1.4.1.4555.10.20.12.1.30018 | kWh | Read
|  |  | PARTIAL RESIDUAL ACTIVE ENERGY (+) |  |  |  | 1.3.6.1.4.1.4555.10.20.12.1.30019 | (1/10) Wh | Read
|  |  | PARTIAL ACTIVE ENERGY (-) |  |  |  | 1.3.6.1.4.1.4555.10.20.12.1.30020 | kWh | Read
|  |  | PARTIAL RESIDUAL ACTIVE ENERGY (-) |  |  |  | 1.3.6.1.4.1.4555.10.20.12.1.30021 | (1/10) Wh | Read
|  |  | PARTIAL REACTIVE ENERGY (+) |  |  |  | 1.3.6.1.4.1.4555.10.20.12.1.30022 | kVarh | Read
|  |  | PARTIAL RESIDUAL REACTIVE ENERGY (+) |  |  |  | 1.3.6.1.4.1.4555.10.20.12.1.30023 | (1/10) Varh | Read
|  |  | PARTIAL REACTIVE ENERGY (-) |  |  |  | 1.3.6.1.4.1.4555.10.20.12.1.30024 | kVarh | Read
|  |  | PARTIAL RESIDUAL REACTIVE ENERGY (-) |  |  |  | 1.3.6.1.4.1.4555.10.20.12.1.30025 | (1/10) Varh | Read
|  |  | PARTIAL APPARENT ENERGY |  |  |  | 1.3.6.1.4.1.4555.10.20.12.1.30034 | kVAh | Read
|  |  | PARTIAL RESIDUAL APPARENT ENERGY |  |  |  | 1.3.6.1.4.1.4555.10.20.12.1.30035 | (1/10) Vah | Read
|  |  | TOTAL HOUR METER |  |  |  | 1.3.6.1.4.1.4555.10.20.12.1.105000 | seconds | Read
|  |  | PARTIAL HOUR METER |  |  |  | 1.3.6.1.4.1.4555.10.20.12.1.105001 | seconds | Read
|  | AC INSTANTANEOUS |  |  |  | 1.3.6.1.4.1.4555.10.20.20
|  |  | CURRENT I1 |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.10000 | mA | Read
|  |  | CURRENT I2 |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.10001 | mA | Read
|  |  | CURRENT I3 |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.10002 | mA | Read
|  |  | CURRENT IN |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.10003 | mA | Read
|  |  | CURRENT Isys |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.10004 | mA | Read
|  |  | CURRENT Idn |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.10005 | mA | Read
|  |  | CURRENT Ipe |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.10006 | mA | Read
|  |  | CURRENT Idir |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.10007 | mA | Read
|  |  | CURRENT Iinv |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.10008 | mA | Read
|  |  | CURRENT Ihom |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.10009 | mA | Read
|  |  | CURRENT Inb |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.10010 | (1/100) % | Read
|  |  | CURRENT Inba |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.10174 | (1/100) % | Read
|  |  | FREQUENCY |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.40000 | mHz | Read
|  |  | POWER FACTOR PF1 |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.75000 | 1/1000 | Read
|  |  | POWER FACTOR PF2 |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.75001 | 1/1000 | Read
|  |  | POWER FACTOR PF3 |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.75002 | 1/1000 | Read
|  |  | POWER FACTOR TOT |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.75003 | 1/1000 | Read
|  |  | POWER FACTOR PF1 TYPE |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.75004 | 1= leading; 2=lagging | Read
|  |  | POWER FACTOR PF2 TYPE |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.75005 | 1= leading; 2=lagging | Read
|  |  | POWER FACTOR PF3 TYPE |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.75006 | 1= leading; 2=lagging | Read
|  |  | POWER FACTOR TOT TYPE |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.75007 | 1= leading; 2=lagging | Read
|  |  | ACTIVE POWER P1 |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.80000 | W | Read
|  |  | ACTIVE POWER P2 |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.80001 | W | Read
|  |  | ACTIVE POWER P3 |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.80002 | W | Read
|  |  | ACTIVE POWER TOT |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.80003 | W | Read
|  |  | REACTIVE POWER Q1 |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.80004 | var | Read
|  |  | REACTIVE POWER Q2 |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.80005 | var | Read
|  |  | REACTIVE POWER Q3 |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.80006 | var | Read
|  |  | REACTIVE POWER TOT |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.80007 | var | Read
|  |  | APPARENT POWER S1 |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.80016 | VA | Read
|  |  | APPARENT POWER S2 |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.80017 | VA | Read
|  |  | APPARENT POWER S3 |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.80018 | VA | Read
|  |  | APPARENT POWER TOT |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.80019 | VA | Read
|  |  | VOLTAGE PH-N V1 |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.110000 | (1/100) V | Read
|  |  | VOLTAGE PH-N V2 |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.110001 | (1/100) V | Read
|  |  | VOLTAGE PH-N V3 |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.110002 | (1/100) V | Read
|  |  | VOLTAGE PH-N VN |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.110003 | (1/100) V | Read
|  |  | VOLTAGE PH-N Vsys |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.110004 | (1/100) V | Read
|  |  | VOLTAGE PH-PH U12 |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.110005 | (1/100) V | Read
|  |  | VOLTAGE PH-PH U23 |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.110006 | (1/100) V | Read
|  |  | VOLTAGE PH-PH U31 |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.110007 | (1/100) V | Read
|  |  | VOLTAGE PH-PH Usys |  |  |  | 1.3.6.1.4.1.4555.10.20.20.1.110008 | (1/100) V | Read
|  | AC INSTANTANEOUS MAX |  |  |  | 1.3.6.1.4.1.4555.10.20.40
|  |  | MAX CURRENT I1 |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.10074 | mA | Read
|  |  | MAX CURRENT I1 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.10075 |  | Read
|  |  | MAX CURRENT I2 |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.10076 | mA | Read
|  |  | MAX CURRENT I2 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.10077 |  | Read
|  |  | MAX CURRENT I3 |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.10078 | mA | Read
|  |  | MAX CURRENT I3 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.10079 |  | Read
|  |  | MAX CURRENT IN |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.10080 | mA | Read
|  |  | MAX CURRENT IN DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.10081 |  | Read
|  |  | MAX FREQUENCY |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.40006 | mHz | Read
|  |  | MAX FREQUENCY DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.40007 |  | Read
|  |  | MAX PF1 |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.75028 | 1/1000 | Read
|  |  | MAX PF1 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.75029 |  | Read
|  |  | MAX PF2 |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.75030 | 1/1000 | Read
|  |  | MAX PF2 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.75031 |  | Read
|  |  | MAX PF3 |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.75032 | 1/1000 | Read
|  |  | MAX PF3 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.75033 |  | Read
|  |  | MAX PF TOT |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.75034 | 1/1000 | Read
|  |  | MAX PF TOT DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.75035 |  | Read
|  |  | MAX P1 |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.80096 | W | Read
|  |  | MAX P1 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.80097 |  | Read
|  |  | MAX P2 |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.80098 | W | Read
|  |  | MAX P2 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.80099 |  | Read
|  |  | MAX P3 |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.80100 | W | Read
|  |  | MAX P3 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.80101 |  | Read
|  |  | MAX P TOT |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.80102 | W | Read
|  |  | MAX P TOT DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.80103 |  | Read
|  |  | MAX Q1 |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.80104 | var | Read
|  |  | MAX Q1 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.80105 |  | Read
|  |  | MAX Q2 |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.80106 | var | Read
|  |  | MAX Q2 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.80107 |  | Read
|  |  | MAX Q3 |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.80108 | var | Read
|  |  | MAX Q3 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.80109 |  | Read
|  |  | MAX Q TOT |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.80110 | var | Read
|  |  | MAX Q TOT DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.80111 |  | Read
|  |  | MAX S1 |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.80120 | VA | Read
|  |  | MAX S1 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.80121 |  | Read
|  |  | MAX S2 |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.80122 | VA | Read
|  |  | MAX S2 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.80123 |  | Read
|  |  | MAX S3 |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.80124 | VA | Read
|  |  | MAX S3 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.80125 |  | Read
|  |  | MAX S TOT |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.80126 | VA | Read
|  |  | MAX S TOT DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.80127 |  | Read
|  |  | MAX VPH-N V1 |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.110098 | (1/100) V | Read
|  |  | MAX VPH-N V1 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.110099 |  | Read
|  |  | MAX VPH-N V2 |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.110100 | (1/100) V | Read
|  |  | MAX VPH-N V2 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.110101 |  | Read
|  |  | MAX VPH-N V3 |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.110102 | (1/100) V | Read
|  |  | MAX VPH-N V3 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.110103 |  | Read
|  |  | MAX VPH-N VN |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.110104 | (1/100) V | Read
|  |  | MAX VPH-N VN DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.110105 |  | Read
|  |  | MAX VPH-PH U12 |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.110108 | (1/100) V | Read
|  |  | MAX VPH-PH U12 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.110109 |  | Read
|  |  | MAX VPH-PH U23 |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.110110 | (1/100) V | Read
|  |  | MAX VPH-PH U23 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.110111 |  | Read
|  |  | MAX VPH-PH U31 |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.110112 | (1/100) V | Read
|  |  | MAX VPH-PH U31 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.40.1.110113 |  | Read
|  | AC INSTANTANEOUS MIN |  |  |  | 1.3.6.1.4.1.4555.10.20.50
|  |  | MIN CURRENT I1 |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.10046 | mA | Read
|  |  | MIN CURRENT I1 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.10047 |  | Read
|  |  | MIN CURRENT I2 |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.10048 | mA | Read
|  |  | MIN CURRENT I2 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.10049 |  | Read
|  |  | MIN CURRENT I3 |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.10050 | mA | Read
|  |  | MIN CURRENT I3 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.10051 |  | Read
|  |  | MIN CURRENT IN |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.10052 | mA | Read
|  |  | MIN CURRENT IN DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.10053 |  | Read
|  |  | MIN FREQUENCY |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.40008 | mHz | Read
|  |  | MIN FREQUENCY DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.40009 |  | Read
|  |  | MIN PF1 |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.75016 | 1/1000 | Read
|  |  | MIN PF1 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.75017 |  | Read
|  |  | MIN PF2 |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.75018 | 1/1000 | Read
|  |  | MIN PF2 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.75019 |  | Read
|  |  | MIN PF3 |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.75020 | 1/1000 | Read
|  |  | MIN PF3 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.75021 |  | Read
|  |  | MIN PF TOT |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.75022 | 1/1000 | Read
|  |  | MIN PF TOT DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.75023 |  | Read
|  |  | MIN P1 |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.80056 | W | Read
|  |  | MIN P1 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.80057 |  | Read
|  |  | MIN P2 |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.80058 | W | Read
|  |  | MIN P2 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.80059 |  | Read
|  |  | MIN P3 |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.80060 | W | Read
|  |  | MIN P3 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.80061 |  | Read
|  |  | MIN P TOT |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.80062 | W | Read
|  |  | MIN P TOT DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.80063 |  | Read
|  |  | MIN Q1 |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.80064 | var | Read
|  |  | MIN Q1 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.80065 |  | Read
|  |  | MIN Q2 |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.80066 | var | Read
|  |  | MIN Q2 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.80067 |  | Read
|  |  | MIN Q3 |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.80068 | var | Read
|  |  | MIN Q3 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.80069 |  | Read
|  |  | MIN Q TOT |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.80070 | var | Read
|  |  | MIN Q TOT DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.80071 |  | Read
|  |  | MIN S1 |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.80080 | VA | Read
|  |  | MIN S1 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.80081 |  | Read
|  |  | MIN S2 |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.80082 | VA | Read
|  |  | MIN S2 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.80083 |  | Read
|  |  | MIN S3 |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.80084 | VA | Read
|  |  | MIN S3 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.80085 |  | Read
|  |  | MIN S TOT |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.80086 | VA | Read
|  |  | MIN S TOT DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.80087 |  | Read
|  |  | MIN VPH-N V1 |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.110060 | (1/100) V | Read
|  |  | MIN VPH-N V1 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.110061 |  | Read
|  |  | MIN VPH-N V2 |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.110062 | (1/100) V | Read
|  |  | MIN VPH-N V2 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.110063 |  | Read
|  |  | MIN VPH-N V3 |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.110064 | (1/100) V | Read
|  |  | MIN VPH-N V3 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.110065 |  | Read
|  |  | MIN VPH-N VN |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.110066 | (1/100) V | Read
|  |  | MIN VPH-N VN DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.110067 |  | Read
|  |  | MIN VPH-PH U12 |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.110070 | (1/100) V | Read
|  |  | MIN VPH-PH U12 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.110071 |  | Read
|  |  | MIN VPH-PH U23 |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.110072 | (1/100) V | Read
|  |  | MIN VPH-PH U23 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.110073 |  | Read
|  |  | MIN VPH-PH U31 |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.110074 | (1/100) V | Read
|  |  | MIN VPH-PH U31 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.50.1.110075 |  | Read
|  | AC AVERAGE |  |  |  | 1.3.6.1.4.1.4555.10.20.30
|  |  | CURRENT I1 |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.10023 | mA | Read
|  |  | CURRENT I2 |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.10024 | mA | Read
|  |  | CURRENT I3 |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.10025 | mA | Read
|  |  | CURRENT IN |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.10026 | mA | Read
|  |  | CURRENT Isys |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.10027 | mA | Read
|  |  | CURRENT Idn |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.10028 | mA | Read
|  |  | CURRENT Ipe |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.10029 | mA | Read
|  |  | CURRENT Idir |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.10030 | mA | Read
|  |  | CURRENT Iinv |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.10031 | mA | Read
|  |  | CURRENT Ihom |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.10032 | mA | Read
|  |  | CURRENT Inb |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.10033 | (1/100) % | Read
|  |  | CURRENT Inba |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.10175 | (1/100) % | Read
|  |  | FREQUENCY |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.40001 | mHz | Read
|  |  | POWER FACTOR PF1 |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.75008 | 1/1000 | Read
|  |  | POWER FACTOR PF2 |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.75009 | 1/1000 | Read
|  |  | POWER FACTOR PF3 |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.75010 | 1/1000 | Read
|  |  | POWER FACTOR TOT |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.75011 | 1/1000 | Read
|  |  | POWER FACTOR PF1 TYPE |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.75012 | 1= leading; 2=lagging | Read
|  |  | POWER FACTOR PF2 TYPE |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.75013 | 1= leading; 2=lagging | Read
|  |  | POWER FACTOR PF3 TYPE |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.75014 | 1= leading; 2=lagging | Read
|  |  | POWER FACTOR TOT TYPE |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.75015 | 1= leading; 2=lagging | Read
|  |  | ACTIVE POWER P1 |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.80028 | W | Read
|  |  | ACTIVE POWER P2 |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.80029 | W | Read
|  |  | ACTIVE POWER P3 |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.80030 | W | Read
|  |  | ACTIVE POWER TOT |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.80031 | W | Read
|  |  | REACTIVE POWER Q1 |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.80032 | var | Read
|  |  | REACTIVE POWER Q2 |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.80033 | var | Read
|  |  | REACTIVE POWER Q3 |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.80034 | var | Read
|  |  | REACTIVE POWER TOT |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.80035 | var | Read
|  |  | APPARENT POWER S1 |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.80044 | VA | Read
|  |  | APPARENT POWER S2 |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.80045 | VA | Read
|  |  | APPARENT POWER S3 |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.80046 | VA | Read
|  |  | APPARENT POWER TOT |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.80047 | VA | Read
|  |  | VOLTAGE PH-N V1 |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.110030 | (1/100) V | Read
|  |  | VOLTAGE PH-N V2 |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.110031 | (1/100) V | Read
|  |  | VOLTAGE PH-N V3 |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.110032 | (1/100) V | Read
|  |  | VOLTAGE PH-N VN |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.110033 | (1/100) V | Read
|  |  | VOLTAGE PH-N Vsys |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.110034 | (1/100) V | Read
|  |  | VOLTAGE PH-PH U12 |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.110035 | (1/100) V | Read
|  |  | VOLTAGE PH-PH U23 |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.110036 | (1/100) V | Read
|  |  | VOLTAGE PH-PH U31 |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.110037 | (1/100) V | Read
|  |  | VOLTAGE PH-PH Usys |  |  |  | 1.3.6.1.4.1.4555.10.20.30.1.110038 | (1/100) V | Read
|  | AC AVERAGE MAX |  |  |  | 1.3.6.1.4.1.4555.10.20.60
|  |  | MAX CURRENT I1 |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.10129 | mA | Read
|  |  | MAX CURRENT I1 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.10130 |  | Read
|  |  | MAX CURRENT I2 |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.10131 | mA | Read
|  |  | MAX CURRENT I2 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.10132 |  | Read
|  |  | MAX CURRENT I3 |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.10133 | mA | Read
|  |  | MAX CURRENT I3 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.10134 |  | Read
|  |  | MAX CURRENT IN |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.10135 | mA | Read
|  |  | MAX CURRENT IN DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.10136 |  | Read
|  |  | MAX FREQUENCY |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.40010 | mHz | Read
|  |  | MAX FREQUENCY DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.40011 |  | Read
|  |  | MAX PF1 |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.75052 | 1/1000 | Read
|  |  | MAX PF1 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.75053 |  | Read
|  |  | MAX PF2 |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.75054 | 1/1000 | Read
|  |  | MAX PF2 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.75055 |  | Read
|  |  | MAX PF3 |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.75056 | 1/1000 | Read
|  |  | MAX PF3 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.75057 |  | Read
|  |  | MAX PF TOT |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.75058 | 1/1000 | Read
|  |  | MAX PF TOT DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.75059 |  | Read
|  |  | MAX P1 |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.80176 | W | Read
|  |  | MAX P1 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.80177 |  | Read
|  |  | MAX P2 |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.80178 | W | Read
|  |  | MAX P2 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.80179 |  | Read
|  |  | MAX P3 |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.80180 | W | Read
|  |  | MAX P3 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.80181 |  | Read
|  |  | MAX P TOT |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.80182 | W | Read
|  |  | MAX P TOT DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.80183 |  | Read
|  |  | MAX Q1 |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.80184 | var | Read
|  |  | MAX Q1 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.80185 |  | Read
|  |  | MAX Q2 |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.80186 | var | Read
|  |  | MAX Q2 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.80187 |  | Read
|  |  | MAX Q3 |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.80188 | var | Read
|  |  | MAX Q3 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.80189 |  | Read
|  |  | MAX Q TOT |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.80190 | var | Read
|  |  | MAX Q TOT DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.80191 |  | Read
|  |  | MAX S1 |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.80200 | VA | Read
|  |  | MAX S1 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.80201 |  | Read
|  |  | MAX S2 |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.80202 | VA | Read
|  |  | MAX S2 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.80203 |  | Read
|  |  | MAX S3 |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.80204 | VA | Read
|  |  | MAX S3 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.80205 |  | Read
|  |  | MAX S TOT |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.80206 | VA | Read
|  |  | MAX S TOT DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.80207 |  | Read
|  |  | MAX VPH-N V1 |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.110175 | (1/100) V | Read
|  |  | MAX VPH-N V1 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.110176 |  | Read
|  |  | MAX VPH-N V2 |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.110177 | (1/100) V | Read
|  |  | MAX VPH-N V2 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.110178 |  | Read
|  |  | MAX VPH-N V3 |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.110179 | (1/100) V | Read
|  |  | MAX VPH-N V3 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.110180 |  | Read
|  |  | MAX VPH-N VN |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.110181 | (1/100) V | Read
|  |  | MAX VPH-N VN DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.110182 |  | Read
|  |  | MAX VPH-PH U12 |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.110185 | (1/100) V | Read
|  |  | MAX VPH-PH U12 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.110186 |  | Read
|  |  | MAX VPH-PH U23 |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.110187 | (1/100) V | Read
|  |  | MAX VPH-PH U23 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.110188 |  | Read
|  |  | MAX VPH-PH U31 |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.110189 | (1/100) V | Read
|  |  | MAX VPH-PH U31 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.60.1.110190 |  | Read
|  | AC AVERAGE MIN |  |  |  | 1.3.6.1.4.1.4555.10.20.70
|  |  | MIN CURRENT I1 |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.10101 | mA | Read
|  |  | MIN CURRENT I1 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.10102 |  | Read
|  |  | MIN CURRENT I2 |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.10103 | mA | Read
|  |  | MIN CURRENT I2 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.10104 |  | Read
|  |  | MIN CURRENT I3 |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.10105 | mA | Read
|  |  | MIN CURRENT I3 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.10106 |  | Read
|  |  | MIN CURRENT IN |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.10107 | mA | Read
|  |  | MIN CURRENT IN DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.10108 |  | Read
|  |  | MIN FREQUENCY |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.40012 | mHz | Read
|  |  | MIN FREQUENCY DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.40013 |  | Read
|  |  | MIN PF1 |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.75040 | 1/1000 | Read
|  |  | MIN PF1 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.75041 |  | Read
|  |  | MIN PF2 |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.75042 | 1/1000 | Read
|  |  | MIN PF2 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.75043 |  | Read
|  |  | MIN PF3 |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.75044 | 1/1000 | Read
|  |  | MIN PF3 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.75045 |  | Read
|  |  | MIN PF TOT |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.75046 | 1/1000 | Read
|  |  | MIN PF TOT DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.75047 |  | Read
|  |  | MIN P1 |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.80136 | W | Read
|  |  | MIN P1 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.80137 |  | Read
|  |  | MIN P2 |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.80138 | W | Read
|  |  | MIN P2 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.80139 |  | Read
|  |  | MIN P3 |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.80140 | W | Read
|  |  | MIN P3 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.80141 |  | Read
|  |  | MIN P TOT |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.80142 | W | Read
|  |  | MIN P TOT DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.80143 |  | Read
|  |  | MIN Q1 |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.80144 | var | Read
|  |  | MIN Q1 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.80145 |  | Read
|  |  | MIN Q2 |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.80146 | var | Read
|  |  | MIN Q2 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.80147 |  | Read
|  |  | MIN Q3 |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.80148 | var | Read
|  |  | MIN Q3 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.80149 |  | Read
|  |  | MIN Q TOT |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.80150 | var | Read
|  |  | MIN Q TOT DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.80151 |  | Read
|  |  | MIN S1 |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.80160 | VA | Read
|  |  | MIN S1 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.80161 |  | Read
|  |  | MIN S2 |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.80162 | VA | Read
|  |  | MIN S2 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.80163 |  | Read
|  |  | MIN S3 |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.80164 | VA | Read
|  |  | MIN S3 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.80165 |  | Read
|  |  | MIN S TOT |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.80166 | VA | Read
|  |  | MIN S TOT DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.80167 |  | Read
|  |  | MIN VPH-N V1 |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.110136 | (1/100) V | Read
|  |  | MIN VPH-N V1 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.110137 |  | Read
|  |  | MIN VPH-N V2 |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.110138 | (1/100) V | Read
|  |  | MIN VPH-N V2 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.110139 |  | Read
|  |  | MIN VPH-N V3 |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.110140 | (1/100) V | Read
|  |  | MIN VPH-N V3 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.110141 |  | Read
|  |  | MIN VPH-N VN |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.110142 | (1/100) V | Read
|  |  | MIN VPH-N VN DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.110143 |  | Read
|  |  | MIN VPH-PH U12 |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.110146 | (1/100) V | Read
|  |  | MIN VPH-PH U12 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.110147 |  | Read
|  |  | MIN VPH-PH U23 |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.110148 | (1/100) V | Read
|  |  | MIN VPH-PH U23 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.110149 |  | Read
|  |  | MIN VPH-PH U31 |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.110150 | (1/100) V | Read
|  |  | MIN VPH-PH U31 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.70.1.110151 |  | Read
|  | AC INST THD CURRENT |  |  |  | 1.3.6.1.4.1.4555.10.20.81
|  |  | THD I1 |  |  |  | 1.3.6.1.4.1.4555.10.20.81.1.100006 | (1/100) % | Read
|  |  | THD I2 |  |  |  | 1.3.6.1.4.1.4555.10.20.81.1.100007 | (1/100) % | Read
|  |  | THD I3 |  |  |  | 1.3.6.1.4.1.4555.10.20.81.1.100008 | (1/100) % | Read
|  |  | THD IN |  |  |  | 1.3.6.1.4.1.4555.10.20.81.1.100009 | (1/100) % | Read
|  |  | MAX THD I1 |  |  |  | 1.3.6.1.4.1.4555.10.20.81.1.100010 | (1/100) % | Read
|  |  | MAX THD I1 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.81.1.100011 |  | Read
|  |  | MAX THD I2 |  |  |  | 1.3.6.1.4.1.4555.10.20.81.1.100012 | (1/100) % | Read
|  |  | MAX THD I2 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.81.1.100013 |  | Read
|  |  | MAX THD I3 |  |  |  | 1.3.6.1.4.1.4555.10.20.81.1.100014 | (1/100) % | Read
|  |  | MAX THD I3 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.81.1.100015 |  | Read
|  |  | MAX THD IN |  |  |  | 1.3.6.1.4.1.4555.10.20.81.1.100016 | (1/100) % | Read
|  |  | MAX THD IN DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.81.1.100017 |  | Read
|  |  | MIN THD I1 |  |  |  | 1.3.6.1.4.1.4555.10.20.81.1.100018 | (1/100) % | Read
|  |  | MIN THD I1 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.81.1.100019 |  | Read
|  |  | MIN THD I2 |  |  |  | 1.3.6.1.4.1.4555.10.20.81.1.100020 | (1/100) % | Read
|  |  | MIN THD I2 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.81.1.100021 |  | Read
|  |  | MIN THD I3 |  |  |  | 1.3.6.1.4.1.4555.10.20.81.1.100022 | (1/100) % | Read
|  |  | MIN THD I3 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.81.1.100023 |  | Read
|  |  | MIN THD IN |  |  |  | 1.3.6.1.4.1.4555.10.20.81.1.100024 | (1/100) % | Read
|  |  | MIN THD IN DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.81.1.100025 |  | Read
|  | AC INST THD VOLTAGE |  |  |  | 1.3.6.1.4.1.4555.10.20.82
|  |  | THD V1 |  |  |  | 1.3.6.1.4.1.4555.10.20.82.1.100000 | (1/100) % | Read
|  |  | THD V2 |  |  |  | 1.3.6.1.4.1.4555.10.20.82.1.100001 | (1/100) % | Read
|  |  | THD V3 |  |  |  | 1.3.6.1.4.1.4555.10.20.82.1.100002 | (1/100) % | Read
|  |  | THD U12 |  |  |  | 1.3.6.1.4.1.4555.10.20.82.1.100003 | (1/100) % | Read
|  |  | THD U23 |  |  |  | 1.3.6.1.4.1.4555.10.20.82.1.100004 | (1/100) % | Read
|  |  | THD U31 |  |  |  | 1.3.6.1.4.1.4555.10.20.82.1.100005 | (1/100) % | Read
|  |  | MAX THD V1 |  |  |  | 1.3.6.1.4.1.4555.10.20.82.1.100032 | (1/100) % | Read
|  |  | MAX THD V1 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.82.1.100033 |  | Read
|  |  | MAX THD V2 |  |  |  | 1.3.6.1.4.1.4555.10.20.82.1.100034 | (1/100) % | Read
|  |  | MAX THD V2 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.82.1.100035 |  | Read
|  |  | MAX THD V3 |  |  |  | 1.3.6.1.4.1.4555.10.20.82.1.100036 | (1/100) % | Read
|  |  | MAX THD V3 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.82.1.100037 |  | Read
|  |  | MAX THD U12 |  |  |  | 1.3.6.1.4.1.4555.10.20.82.1.100038 | (1/100) % | Read
|  |  | MAX THD U12 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.82.1.100039 |  | Read
|  |  | MAX THD U23 |  |  |  | 1.3.6.1.4.1.4555.10.20.82.1.100040 | (1/100) % | Read
|  |  | MAX THD U23 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.82.1.100041 |  | Read
|  |  | MAX THD U31 |  |  |  | 1.3.6.1.4.1.4555.10.20.82.1.100042 | (1/100) % | Read
|  |  | MAX THD U31 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.82.1.100043 |  | Read
|  |  | MIN THD V1 |  |  |  | 1.3.6.1.4.1.4555.10.20.82.1.100044 | (1/100) % | Read
|  |  | MIN THD V1 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.82.1.100045 |  | Read
|  |  | MIN THD V2 |  |  |  | 1.3.6.1.4.1.4555.10.20.82.1.100046 | (1/100) % | Read
|  |  | MIN THD V2 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.82.1.100047 |  | Read
|  |  | MIN THD V3 |  |  |  | 1.3.6.1.4.1.4555.10.20.82.1.100048 | (1/100) % | Read
|  |  | MIN THD V3 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.82.1.100049 |  | Read
|  |  | MIN THD U12 |  |  |  | 1.3.6.1.4.1.4555.10.20.82.1.100050 | (1/100) % | Read
|  |  | MIN THD U12 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.82.1.100051 |  | Read
|  |  | MIN THD U23 |  |  |  | 1.3.6.1.4.1.4555.10.20.82.1.100052 | (1/100) % | Read
|  |  | MIN THD U23 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.82.1.100053 |  | Read
|  |  | MIN THD U31 |  |  |  | 1.3.6.1.4.1.4555.10.20.82.1.100054 | (1/100) % | Read
|  |  | MIN THD U31 DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.82.1.100055 |  | Read
|  | DC MEASUREMENTS |  |  |  | 1.3.6.1.4.1.4555.10.20.90
|  |  | I RMS INST |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.10176 | mA | Read
|  |  | I DC INST |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.10177 | mA | Read
|  |  | I RIPPLE INST |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.10178 | mA | Read
|  |  | I RMS AVG |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.10179 | mA | Read
|  |  | I DC AVG |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.10180 | mA | Read
|  |  | I RIPPLE AVG |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.10181 | mA | Read
|  |  | I RMS INST MAX |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.10268 | mA | Read
|  |  | I RMS INST MAX DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.10269 |  | Read
|  |  | I DC INST MAX |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.10270 | mA | Read
|  |  | I DC INST MAX DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.10271 |  | Read
|  |  | I RIPPLE INST MAX |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.10272 | mA | Read
|  |  | I RIPPLE INST MAX DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.10273 |  | Read
|  |  | I RMS INST MIN |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.10274 | mA | Read
|  |  | I RMS INST MIN DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.10275 |  | Read
|  |  | I DC INST MIN |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.10276 | mA | Read
|  |  | I DC INST MIN DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.10277 |  | Read
|  |  | I RIPPLE INST MIN |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.10278 | mA | Read
|  |  | I RIPPLE INST MIN DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.10279 |  | Read
|  |  | I RMS AVG MAX |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.10281 | mA | Read
|  |  | I RMS AVG MAX DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.10282 |  | Read
|  |  | I DC AVG MAX |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.10283 | mA | Read
|  |  | I DC AVG MAX DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.10284 |  | Read
|  |  | I RIPPLE AVG MAX |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.10285 | mA | Read
|  |  | I RIPPLE AVG MAX DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.10286 |  | Read
|  |  | I RMS AVG MIN |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.10287 | mA | Read
|  |  | I RMS AVG MIN DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.10288 |  | Read
|  |  | I DC AVG MIN |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.10289 | mA | Read
|  |  | I DC AVG MIN DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.10290 |  | Read
|  |  | I RIPPLE AVG MIN |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.10291 | mA | Read
|  |  | I RIPPLE AVG MIN DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.10292 |  | Read
|  |  | P DC INST |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.80003 | W | Read
|  |  | P DC AVG |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.80031 | W | Read
|  |  | P DC INST MIN |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.80062 | W | Read
|  |  | P DC INST MIN DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.80063 |  | Read
|  |  | P DC INST MAX |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.80102 | W | Read
|  |  | P DC INST MAX DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.80103 |  | Read
|  |  | P DC AVG MIN |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.80142 | W | Read
|  |  | P DC AVG MIN DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.80143 |  | Read
|  |  | P DC AVG MAX |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.80182 | W | Read
|  |  | P DC AVG MAX DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.80183 |  | Read
|  |  | V RMS INST |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.110338 | (1/100) V | Read
|  |  | V DC INST |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.110339 | (1/100) V | Read
|  |  | V RIPPLE INST |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.110340 | (1/100) V | Read
|  |  | V RMS AVG |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.110343 | (1/100) V | Read
|  |  | V DC AVG |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.110344 | (1/100) V | Read
|  |  | V RIPPLE AVG |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.110345 | (1/100) V | Read
|  |  | V RMS INST MAX |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.110416 | (1/100) V | Read
|  |  | V RMS INST MAX DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.110417 |  | Read
|  |  | V DC INST MAX |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.110418 | (1/100) V | Read
|  |  | V DC INST MAX DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.110419 |  | Read
|  |  | V RIPPLE INST MAX |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.110420 | (1/100) V | Read
|  |  | V RIPPLE INST MAX DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.110421 |  | Read
|  |  | V RMS INST MIN |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.110422 | (1/100) V | Read
|  |  | V RMS INST MIN DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.110423 |  | Read
|  |  | V DC INST MIN |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.110424 | (1/100) V | Read
|  |  | V DC INST MIN DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.110425 |  | Read
|  |  | V RIPPLE INST MIN |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.110426 | (1/100) V | Read
|  |  | V RIPPLE INST MIN DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.110427 |  | Read
|  |  | V RMS AVG MAX |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.110429 | (1/100) V | Read
|  |  | V RMS AVG MAX DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.110430 |  | Read
|  |  | V DC AVG MAX |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.110431 | (1/100) V | Read
|  |  | V DC AVG MAX DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.110432 |  | Read
|  |  | V RIPPLE AVG MAX |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.110433 | (1/100) V | Read
|  |  | V RIPPLE AVG MAX DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.110434 |  | Read
|  |  | V RMS AVG MIN |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.110435 | (1/100) V | Read
|  |  | V RMS AVG MIN DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.110436 |  | Read
|  |  | V DC AVG MIN |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.110437 | (1/100) V | Read
|  |  | V DC AVG MIN DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.110438 |  | Read
|  |  | V RIPPLE AVG MIN |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.110439 | (1/100) V | Read
|  |  | V RIPPLE AVG MIN DATE |  |  |  | 1.3.6.1.4.1.4555.10.20.90.1.110440 |  | Read
|  | MULTIFLUID PULSE METERS |  |  |  | 1.3.6.1.4.1.4555.10.20.14
|  |  | ENERGY METER PULSE UNIT |  |  |  | 1.3.6.1.4.1.4555.10.20.14.1.65012 |  | Read
|  |  | ENERGY METER PULSE WEIGHT |  |  |  | 1.3.6.1.4.1.4555.10.20.14.1.65013 | (1/100) x WEIGHT | Read
|  |  | TOTAL ENERGY METER |  |  |  | 1.3.6.1.4.1.4555.10.20.14.1.65014 |  | Read
|  |  | PARTIAL ENERGY METER |  |  |  | 1.3.6.1.4.1.4555.10.20.14.1.65015 |  | Read
| PRODUCT INPUT/OUTPUT |  |  |  | 1.3.6.1.4.1.4555.10.30
|  | DIGITAL INPUTS |  |  |  | 1.3.6.1.4.1.4555.10.30.1
|  |  | DIGITAL IN STATUS |  |  |  | 1.3.6.1.4.1.4555.10.30.1.1.90002 | 0=activated; 1=deactivated | Read
|  |  | DIGITAL IN MODE (NO/NC) |  |  |  | 1.3.6.1.4.1.4555.10.30.1.1.90003 |  | Read
|  | DIGITAL OUTPUTS |  |  |  | 1.3.6.1.4.1.4555.10.30.2
|  |  | DIGITAL OUT DEACTIVATE |  |  |  | 1.3.6.1.4.1.4555.10.30.2.1.85177 | Write 1 to deactivate | Read/write
|  |  | DIGITAL OUT ACTIVATE |  |  |  | 1.3.6.1.4.1.4555.10.30.2.1.85178 | Write 1 to activate | Read/write
|  |  | DIGITAL OUT STATUS |  |  |  | 1.3.6.1.4.1.4555.10.30.2.1.90006 | 0=activated; 1=deactivated | Read
|  |  | DIGITAL OUT MODE (NO/NC) |  |  |  | 1.3.6.1.4.1.4555.10.30.2.1.90024 |  | Read
|  | ANALOG INPUTS |  |  |  | 1.3.6.1.4.1.4555.10.30.4
|  |  | INST VALUE |  |  |  | 1.3.6.1.4.1.4555.10.30.4.1.65004 |  | Read
|  |  | AVG VALUE |  |  |  | 1.3.6.1.4.1.4555.10.30.4.1.65093 |  | Read
|  |  | MODE (0-20mA/4-20mA) |  |  |  | 1.3.6.1.4.1.4555.10.30.4.1.65026 | 0=0-20mA; 1=4-20mA | Read
|  |  | UNIT |  |  |  | 1.3.6.1.4.1.4555.10.30.4.1.65027 |  | Read
|  | ANALOG OUTPUTS |  |  |  | 1.3.6.1.4.1.4555.10.30.5
|  |  | INST VALUE |  |  |  | 1.3.6.1.4.1.4555.10.30.5.1.65059 |  | Read
|  |  | AVG VALUE |  |  |  | 1.3.6.1.4.1.4555.10.30.5.1.65060 |  | Read
|  |  | MODE (0-20mA/4-20mA) |  |  |  | 1.3.6.1.4.1.4555.10.30.5.1.65056 | 0=0-20mA; 1=4-20mA | Read
|  | SWITCH/BREAKER MONITORING |  |  |  | 1.3.6.1.4.1.4555.10.30.3
|  |  | PROTECTIVE DEVICE POSITION |  |  |  | 1.3.6.1.4.1.4555.10.30.3.1.90007 | 0=open; 1=closed | Read
|  |  | PROTECTIVE DEVICE TRIP |  |  |  | 1.3.6.1.4.1.4555.10.30.3.1.90008 | 0=No; 1=Yes | Read
|  |  | PROTECTIVE DEVICE TRIP COUNTER |  |  |  | 1.3.6.1.4.1.4555.10.30.3.1.90009 |  | Read
| ATS DATA |  |  |  | 1.3.6.1.4.1.4555.10.40
|  | ATS MEASUREMENTS |  |  |  | 1.3.6.1.4.1.4555.10.40.10
|  |  | VOLTAGE PH-PH U12 SOURCE 1 |  |  |  | 1.3.6.1.4.1.4555.10.40.10.1.135079 | (1/100) V | Read
|  |  | VOLTAGE PH-PH U23 SOURCE 1 |  |  |  | 1.3.6.1.4.1.4555.10.40.10.1.135080 | (1/100) V | Read
|  |  | VOLTAGE PH-PH U31 SOURCE 1 |  |  |  | 1.3.6.1.4.1.4555.10.40.10.1.135081 | (1/100) V | Read
|  |  | VOLTAGE PH-N V1 SOURCE 1 |  |  |  | 1.3.6.1.4.1.4555.10.40.10.1.135082 | (1/100) V | Read
|  |  | VOLTAGE PH-N V2 SOURCE 1 |  |  |  | 1.3.6.1.4.1.4555.10.40.10.1.135083 | (1/100) V | Read
|  |  | VOLTAGE PH-N V3 SOURCE 1 |  |  |  | 1.3.6.1.4.1.4555.10.40.10.1.135084 | (1/100) V | Read
|  |  | FREQUENCY SOURCE 1 |  |  |  | 1.3.6.1.4.1.4555.10.40.10.1.135085 | mHz | Read
|  |  | VOLTAGE PH-PH U12 SOURCE 2 |  |  |  | 1.3.6.1.4.1.4555.10.40.10.1.135086 | (1/100) V | Read
|  |  | VOLTAGE PH-PH U23 SOURCE 2 |  |  |  | 1.3.6.1.4.1.4555.10.40.10.1.135087 | (1/100) V | Read
|  |  | VOLTAGE PH-PH U31 SOURCE 2 |  |  |  | 1.3.6.1.4.1.4555.10.40.10.1.135088 | (1/100) V | Read
|  |  | VOLTAGE PH-N V1 SOURCE 2 |  |  |  | 1.3.6.1.4.1.4555.10.40.10.1.135089 | (1/100) V | Read
|  |  | VOLTAGE PH-N V2 SOURCE 2 |  |  |  | 1.3.6.1.4.1.4555.10.40.10.1.135090 | (1/100) V | Read
|  |  | VOLTAGE PH-N V3 SOURCE 2 |  |  |  | 1.3.6.1.4.1.4555.10.40.10.1.135091 | (1/100) V | Read
|  |  | FREQUENCY SOURCE 2 |  |  |  | 1.3.6.1.4.1.4555.10.40.10.1.135092 | mHz | Read
|  | ATS STATUS |  |  |  | 1.3.6.1.4.1.4555.10.40.50
|  |  | ATS SOURCE PRIORITY |  |  |  | 1.3.6.1.4.1.4555.10.40.50.1.135000 | 0=Network; 1=Source1; 2=Source2 | Read
|  |  | ATS ALARM FAULT CODE |  |  |  | 1.3.6.1.4.1.4555.10.40.50.1.135001 | 0=None; 1=Operating factor; 2=Neutral position; 3=Fault 1; 4=Fault 2; 5=Alarm 1; 6=Alarm 2; 7=Source 1 rotation; 8=Source 2 rotation; 9=Source 1 Capa; 10=Source 2 Capa; 11 = Source 1 Power; 12=Source 2 Power; 13=Position 1; 14=Position 2; 15=Position 0; 16=Fault 0; 17=Source 1 unbalanced; 18=Source 2 unbalanced; 19=Main fault; 20=Motor fault; 21=Autoconfiguration failed; 255=Unknown or Multiple | Read
|  |  | ATS OPERATING MODE |  |  |  | 1.3.6.1.4.1.4555.10.40.50.1.135038 | 0=Manual; 1=Locked; 16=Auto; 32=Remote; 64=Inhibit | Read
|  |  | ATS POSITION |  |  |  | 1.3.6.1.4.1.4555.10.40.50.1.135039 | 0=Unknown; 1=Position 0; 2=Position 1; 3=Position 2 | Read
|  |  | ATS GENERATOR RELAY STATE SOURCE 1 |  |  |  | 1.3.6.1.4.1.4555.10.40.50.1.135041 | 0=Inactive; 1=Active | Read
|  |  | ATS GENERATOR RELAY STATE SOURCE 2 |  |  |  | 1.3.6.1.4.1.4555.10.40.50.1.135042 | 0=Inactive; 1=Active | Read
|  |  | ATS SOURCE 1 STATE |  |  |  | 1.3.6.1.4.1.4555.10.40.50.1.135044 | 0=Under Threshold; 1=Present; 2=Available | Read
|  |  | ATS SOURCE 2 STATE |  |  |  | 1.3.6.1.4.1.4555.10.40.50.1.135045 | 0=Under Threshold; 1=Present; 2=Available | Read
|  |  | ATS TEST IN PROGRESS |  |  |  | 1.3.6.1.4.1.4555.10.40.50.1.135046 | 0=None; 1=TOF; 2=EOF; 4=TOL; 8=EOL | Read
|  |  | ATS OPERATION CYCLE COUNTER |  |  |  | 1.3.6.1.4.1.4555.10.40.50.1.135048 |  | Read
|  |  | ATS OPERATION COUNT POSITION 1 |  |  |  | 1.3.6.1.4.1.4555.10.40.50.1.135049 | 0=No network present for DPS; 1=Source 1 present for DPS; 2=Source 2 present for DPS; 3=Source 1+2 present for DPS | Read
|  |  | ATS OPERATION COUNT POSITION 2 |  |  |  | 1.3.6.1.4.1.4555.10.40.50.1.135050 | 0=No network present for DPS; 1=Source 1 present for DPS; 2=Source 2 present for DPS; 3=Source 1+2 present for DPS | Read
|  |  | ATS FAULT SUMMARY |  |  |  | 1.3.6.1.4.1.4555.10.40.50.1.135052 | 0=None; 1=Alarm; 2=Fault | Read
|  |  | ATS LAST SWITCH-OVER CAUSE |  |  |  | 1.3.6.1.4.1.4555.10.40.50.1.135053 | 0=None; 1=Manual; 2=Under voltage Source 1; 3=Under voltage Source 2; 4=Over voltage Source 1; 5=Over voltage Source 2; 6=Under frequence Source 1; 7=Under frequence Source 2; 8=Over frequence Source 1; 9=Over frequence Source 2; 10=Unbalanced Source 1; 11=Unbalanced Source 2; 12=Rotation Source 1; 13=Rotation Source 2; 14=Priority Source; 15=Remote | Read