TECHNICAL SPECIFICATION

DIRIS A-40

Plug and Play multi-function meter

for the measurement and monitoring of electrical installations

Purpose of the specification

This specification describes a multi-function meter and its associated current sensors designed for measuring and monitoring electrical installations. It is particularly well suited to isolated measuring points which require RS485, Ethernet or Profibus communications.

The technical benchmark reference is SOCOMEC DIRIS A-40 or a similar solution that has been approved by us.

- General characteristics

The measuring device should be a compact 96*96 PMD* compliant with IEC standard 61557-12 and should be UL Listed.

It should provide all voltage, current, power, energy and power quality measurements and enable a joint analysis of single-phase and multi-phase loads (even simultaneously).

It is based on a Plug & Play concept that provides automatic detection of the network type, loads and current sensor ratings and verification of the current flow direction.. A configuration wizard should help the user to configure the product and check the commissing. The product shall be able to correct the wiring mistakes by himself. This function shall be done without any load.

In addition, it offers:

- 4 independent RJ12 type current inputs allowing simultaneous measurement of up to 4 loads (single-phase, three-phase, with or without neutral)

- A native RS485 output in Modbus RTU protocol (with DIRIS A-40 RS version)

- A native Modbus TCP over Ethernet communication and also a RS485 output in Modbus RTU protocol

- A native a Profibus DVP1 communication also a RS485 output in Modbus RTU protocol

- A class 0.5 accuracy on the global measurement chain (PMD + sensors) according to IEC 61557-12

- Monitoring functions dedicated to the protective devices

The device has to panel mounted.

*PMD: Performance Measuring and Monitoring Device in accordance with IEC 61557-12.

The current sensors have to meet the following characteristics:

- Form an integral part of the measuring system and therefore, must come from the same supplier as the Power meters.

- Have a mV output and have an RJ-type connection to the PMD.

- Enable risk free connection and on-load opening of the sensor’s secondary

- Prevent any installation errors, which will be automatically identified (type, rating, current direction) by the PMD. If an error is detected an alarm will be automatically generated.

- Monitor the protective device (see details bellows) without any auxiliary contact wiring

The PMD should be suited for any type of new or existing installation using TE solid-core sensors from 5A to 2000A, iTR split-core sensors from 25A to 600A and TF flexible sensors from 100A to 6000A. No additional calibration of the PMD or the previously stated current sensors has to be done to guarantee the proper functioning of the system.

The solid-core and split-core sensors may be fitted aligned or staggered to match the pitch of the corresponding protective devices.

- Functions and performance

The PMD must respect the following requirements:

- Accuracy of the measurement chain

The combination of the measuring devices and sensors allows the following overall accuracy of the measurement chain to be ensured for power and energy (kWh):

- Class 0.5 in accordance with IEC 61557-12: From 2 to 120% of the rated current for the global measurement chain (measuring device + current sensors)

- Class 0.2 in accordance with IEC 61557-12 and ANSI C12.20: - Accuracy of 0.2% for the measuring device alone

- General measurements

- Current, frequency and voltage parameters

- Active, reactive and apparent power, power factor, cos phi and tan phi

- Operation across 4 quadrants (import/export powers)

- Predictive power

The measurements will be available with the following values:

- instantaneous

- max instantaneous (time-stamped)

- min instantaneous (time-stamped)

- averages

- max averages (time-stamped)

- min averages (time-stamped)

- system

- Power quality analysis

- THD and individual harmonics (up to rank 63) for voltage and current

- Unbalance for voltage and current, symmetrical components (direct, inverse and homopolar)

- Crest factor for voltage and current

- K-factor

- Events in accordance with EN 50160 (voltage sags/dips, voltage swells and voltage interruptions) based on a half-cycle sampling rate

- Current inrush based on a half-cycle sampling rate

- Predictive power

- Metering

- Active, reactive (lagging and leading), apparent partial and total energies

- Load curves / Demand profiles

- Multi-tariff (8 tariffs maximum)

- Multi-fluid metering on pulse input

- Load shedding

- Protection device monitoring without the use of auxiliary contacts

- Number of operations

- Open / cloded position

- Trip count

- Last trip date

- Drawer position

- Alarms

- 8 time-stamped alarms for the instantaneous or average values for an electrical parameter

- 4 alarms for changes in status of a digital input

- Possibility of Boolean combinations of alarms

- Predictive power smart alarm

- System alarm (sensor disconnection,…)

- Data-logging

- Recording of average electrical values (configurable: U, F, I, P, Q, S, PF, THD, Crest factor, K-Factor) with a variable integration period

- Recording and time-stamping of min/max electrical values

- Recording of measurement alarms

- Recording of EN 50160 events and current inrush

- Recording of system alarms

- Inputs/Outputs

- 3 digital inputs suited for multi-fluid metering, pulse meter, state report, tariff synchronisation,

- 2 digital outputs suited for alarming, energy pulse, load shedding or command

- Communication

- Modbus RS485 communication (DIRIS A-40 RS version)

- Modbus RS485 communication + Ethernet  (DIRIS A-40 RS + Ethernet version) / Possible to switch to bacNet IP

- Modbus RS485 communication + Profibus  (DIRIS A-40 RS + Profibus DPV1 version)

- Webserver (only for Ethernet version)

All data from the PMD shall be visualized in an embedded web interface. This webserver shall allow:

- Display of real-time and historical measurements (load curves and energy consumptions log

- Display of on-going alarms and a log of finished alarms

- The PMD display should have the following characteristics:

- High-resolution & graphical views

- IP65 degree of protection for the front panel

- 10 direct access keys to the configuration and measuring information

- Software correction (for circuits up to 600A)

Software correction of wiring errors, even in off-load conditions by pressing a front button on the module. This functionality shall be available when current sensors are positioned downstream any protection device.

The measurement system can also be configured via a USB connection or via the communication network (RS485/Ethernet) using a remote Display or a dedicated and free configuration software.