SECTION 26 36 23

AUTOMATIC TRANSFER SWITCHES EQUIPMENT

PART 1 – GENERAL

  - SUMMARY

- This section includes automatic transfer switches equipment.

- All ATSE is to be designed as one integrated product (power switching, motorisation and ATS Control), shall be of the same recognized manufacturer and shall be tested to IEC 60947-6-1 as one complete automatic transfer switch.

  - SUBMITTALS

- Product data including: rated operational voltage and current capacity, number of poles (fully rated) and characteristics according to IEC 60947-6-1 and IEC 60947-3.

- Metric dimensional drawings issued by the manufacturer for the complete ATSE including front, side and top views together with provision for power terminal connections.

- Instructions for back plate and flush mounting installation of the ATSE within an enclosure.

- Instruction manual specific to the ATSE, published in the English language by the manufacturer.

- Quick Start Instruction sheet specific to the ATSE and published by the manufacturer.

- Quality control test reports issued by the manufacturer for the ATSE.

- A certificate issued by the manufacturer to certify that the ATSE supplied is in full compliance with the requirements included in this specification.

  - STANDARDS AND QUALITY ASSURANCE

- The ATSE supplied must comply with Class PC of IEC 60947-6-1: (Low-voltage switchgear and control gear - Multiple function equipment – Transfer switching equipment).

- Besides IEC 60947-6-1 the ATSE supplied must also comply with IEC 60947-3: (Low-voltage switchgear and control gear – Switches, disconnectors, switch-disconnectors and fuse-combination units).

- The ATSE supplied is to be designed and built as a fully integrated product (power switching, motorisation and ATS Control), shall be of the same recognized manufacturer and shall be tested to IEC 60947-6-1 as one complete unit.

- The ATSE label shall include data markings and compliance to IEC 60947-6-1 and IEC 60947-3.

- The manufacturer shall be certified ISO 9001: 2008 with third party certification verifying its Quality Assurance in design and production in accordance with ISO 9001.

PART 2 – PRODUCTS

  - ACCEPTABLE ATSE and MANUFACTURERS

- The ATSE shall be in full compliance with this specification and will be one of the following :

  - SOCOMEC “ATyS g ”.

  - …..

  - GENERAL CONSTRUCTION

- The ATSE shall be composed of :

  - An open transition break before make architecture (I – 0 – II), in full compliance with IEC 60947-6-1 Class PC.

  - Two back to back, fully rated, IEC 60947-3 compliant, load break switch disconnects.

  - A maintenance free switch design that includes self-cleaning contacts on all poles.

  - An inherent fully integrated robust mechanical interlock between both switches.

  - An independent switching mechanism free from external factors during transfer.

  - Mounting lugs fit onto the switches (power section) independent of the motorisation.

  - A wide band (control voltage of 50/60Hz, 166-332Vac) motorisation module fit directly to the switching mechanism.

  - An integrated ATS controller with dual power supply (DPS) and 3 phase sensing on both source supplies. (Monitoring device and control module - MDCM).

  - An easy to remove motorisation & control module. (With no disturbance to the load).

  - Dual emergency manual operation.

  - Padlocking in the zero position with the use of up to 3x 8mm padlocks.

  - Clear switch position indication (I – 0 – II), on the motorisation module.

- The ATSE shall be fully integrated in one device:

Besides customer I/O, no additional wiring between functional units other than the power connections and voltage sensing shall be necessary to allow the proper functioning of the ATSE.

- The ATSE should include dual “Product Available Outputs” (one on the motorisation and one on the ATS controls). The product should analyse / test its condition periodically and communicate through dry contacts to report the ability of the transfer switching equipment to operate.

  - RATINGS AND ATSE TEST

- Characteristics, nominal phase voltage, current ratings, number of poles and withstand ratings shall be as shown on the drawings. The ampere ratings shall be for 100% continuous load current with the neutral pole fully rated.

- Ratings and characteristics shall be according to IEC 60947-6-1 and IEC 60947-3 with non-welding of contacts during the performance of withstand and closing tests.

- The complete ATSE shall be fully factory assembled by the manufacturer and tested to IEC 60947-6-1 so as to ensure proper operation of the ATSE as a complete system with a good overall operation sequence. The test must also ensure that the operating transfer time, voltage, frequency and time delay settings are in compliance with the specification requirements.

  - DESIGN REQUIREMENTS:

- The ATSE shall have 3 stables positions: I – 0 - II.

- Besides the ATSE features as per IEC 60947-6-1, the equipment shall be a Load Break and Disconnect switch as per IEC 60947-3 with padlocking with a minimum of one padlock only.

- The ATSE shall be of the clearly visible position indication type with markings I - 0 - II

- The ATSE shall be electrically operated and fully automatic with the possibility to override the automation and operate remotely via dry contact inputs for position orders.

- Dual emergency manual operation shall be provided using an insulated handle directly through the motorisation and on the switch mechanism with the motorisation removed.

- The ATSE shall integrate a wide band (50/60Hz, 166-332Vac) double power supply (DPS) to supply the aux power to the motorisation and ATS immaterial of the available supply source.

- The ATSE shall have a distinct manual / automatic mode selectable by turning a rotary switch or a removable key switch located on the motorisation module.

- The neutral pole of the ATSE switches shall be fully rated and left or right configuration.

- The ATSE shall have no power consumption while in a stable position other than that required for the ATS control unit.

- The 4 poles shall switch simultaneously with a time gap of less than 1ms to avoid potential floating neutral issues during switching.

  - SAFETY REQUIREMENTS & FEATURES:

- Under no circumstance (including equipment failure) should it be possible to close switch I and switch II simultaneously.

- During manual operation, opening and closing of the contacts must be independent from the emergency handle operational speed.

- The ATSE shall have a built-in provision for padlocking in the O position. One x4mm padlock should be sufficient to padlock whilst it should be possible to use up to 3x 8mm padlocks.

- All operating modes shall be inhibited when the product is padlocked.

- Padlocking shall only be possible with the mode selector switch in manual position.

- An insulated emergency handle shall be provided for dual manual operation.

- The ATSE should allow manual switching I-0-II at full load without damage to the contacts.

  - BASIC OPERATION:

- The ATSE should have distinct Auto and Manual operational modes that should be fully operational under any load condition. (Within the product ratings intended scope).

- The aux power of the ATSE shall be supplied by any one of the available supplies through a built-in dual power supply (DPS).

- The ATSE power section shall have a high short time withstand current capability. (Icw 1s)

- An automatic retransfer function should be included with the facility to inhibit retransfer locally or remotely through dry contacts.

- The ATSE shall have the facility to inhibit the ATS controller and electrically change the switch state to any position (I – 0 – II) through dedicated inputs and dry contacts.

- The ATSE shall include a priority input to force the switch to the 0 position and inhibit the automation of the ATS controller.

- Cable length for remote dry contact order inputs is to be ≤ 100m

  - ATS CONTROLS:

- The ATSE shall have a fully integrated ATS Controller fixed directly on the motorisation.

- The controller shall include DIP switches, potentiometers and LED’s with front access.

- Electrical motorised control (position I, O, II) remotely through dry contacts and optionally through communication.

- Main Parameters:

- The ATS controller shall include 3 phase and neutral sensing for the monitoring of voltage and frequency on both source supplies.

- Voltage and Frequency settings shall be field adjustable in % of the nominal value..

- Setting configuration shall be adjustable through DIP switches and potentiometers on the front face.

- The ATS Controller shall have phase sequence detection.

- Changeover shall be forbidden if the supply phase sequences are different.

- The ATS Controller is to include an Auto-Configuration function for configuration of the source supply voltage, frequency, phase rotation and neutral position.

- The ATS Controller shall have the possibility to select the network type.

- The ATS Controller shall allow the setting of the source priority.

  - ATSE INTERFACE:

- The ATS Controller is to be easily configurable via DIP switches and potentiometers directly on the controller

- Status of the ATSE shall be clearly visible through LED’s on the front of the unit.

  - ATSE INPUTS & OUTPUTS:

- The ATSE shall include five fixed output contacts, for positions I-0-II, for the availability of the product (motorisation watchdog) and a genset start relay.

- The genset start relay is to be a failsafe 3 point changeover NO/NC dry contact.

- The ATSE shall have five fixed inputs on the motorization module: one to enable the remote inputs and inhibit the automation, three to remotely control the switch positions, and one priority input to force the product to the 0 position.

- The ATSE shall be able to provide

- six programmable inputs and one programmable out with the option to expand an additional eight programmable inputs and eight programmable outputs.

  - COMMUNICATION:

- The ATSE is to include the possibility to plug in an optional communication modules with RS 485 Modbus.

- Monitoring software is to be available free on the manufacturer’s website.

- Monitoring and control through software is to be password protected.

  - TIMER SETTINGS:

- An adjustable timer of 0 to 60 seconds shall be provided to detect source 1 or source 2 failures, and to override any transient outages of the normal supply. (Source Failure Timer, FT).

- A possibility to stay in switch position 0 shall be provided with an adjustment of 0 or 2 seconds prior to switch over the available source (0DT Timer).

- An adjustable timer of 0 to 60 minutes shall be provided to detect priority network return to normal so as to override any incorrect availability of the normal supply. (Main Return Timer, RT).

- A fixed timer of 4 minutes shall be provided to allow the generator to cool down after the load retransfer from alternative back to the normal supply. (Embedded Cool Down Timer, CT).

  - ON LOAD / OFF LOAD TESTS:

- The ATSE should include for On-Load as well as Off Loads tests associated with Mains – Gen applications. (The test will as a minimum start the Genset for a determined period of time). These tests should be operable through remote inputs, through MODBUS communication or through the ATSE monitoring software.

  - ONLINE MAINTENANCE:

- Once installed, the ATSE shall be “Maintenance Free” however it would be recommended to switch through at least one complete cycle once a year.

- Replacement of the electrical parts (motorization or ATS controller) shall be possible on-load without removal of or disturbance to the power section and load.

- Once the motorisation module is removed the transfer switch shall remain functional as an on-load manually operated transfer switch. The switching mechanism should be independent of the operator switching speed.

  - EMC:

- The ATSE should be designed and built in accordance with IEC 60947-1 standards for EMC  (Products intended to be installed in an "Industrial, Commercial and/or Residential Environment" therefore respecting both Class A and/or Class B EMC requirements as described below.

| Description | Std (IEC) | Requirement (criteria) |
| --- | --- | --- |
| Conducted | CISPR 11 | Class B |
| Radiated | CISPR 11 | Class B |
| ESD contact | 61000-4-2 | 4KV (B) |
| ESD air | 61000-4-2 | 8KV (B) |
| Electromagnetic field | 61000-4-3 | 10V/m (A) |
| RF Conducted | 61000-4-6 | 10V (A) |
| Burst | 61000-4-4 | 2KV (B) power 1KV (B) control |
| Surge Common | 61000-4-5 | 2KV (B) |
| Surge differential | 61000-4-5 | 1KV (B) |

PART 3 – EXECUTION

3.01	INSTALLATION:

- Preparation shall be in accordance with the reviewed product data, final shop drawings and the manufacturer’s recommendations.

- Installation shall be in accordance with manufacturer’s instructions and recommendations.

- Identify components according to Division 26 section “Identification for Electrical Systems”.

3.02	CONNECTION:

- Wiring for the ATSE equipment shall be in accordance with manufacturer’s instructions.

- Connections and wiring shall be according to Division 26 section “low-Voltage Electrical Power Conductors and cables”.

3.03	MAINTENANCE & TRAINING:

- Operational and Maintenance Instructions:  Personnel on site should be formally trained by the manufacturer’s authorized representative. This is with regards to the proper operation and maintenance of the automatic transfer switching equipment.

3.04	TESTING:

- The ATSE shall be declared compliant to the IEC standards listed above by a testing laboratory having delegation or working under contract for certification to UL and IEC standards under the IEC Electrotechnical Equipment (IECEE) certification body scheme.

- After installation of the equipment, a test report is to be submitted to state that the equipment has been installed and commissioned in accordance with the manufacturer’s instructions.

END OF SECTION 26 36 23