TECHNICAL SPECIFICATION

Power Conversion for Energy Storage Systems (PCS)

RATED POWER from 33 kVA to 200kVA – Three-phase

TABLE OF CONTENTS

ABBREVIATIONS	2

USER GUIDE	2

1.	PURPOSE OF THE SPECIFICATION DOCUMENT	2

2.	NORMATIVE COMPLIANCE	3

3.	ORIGIN	3

4.	GLOBAL DESCRIPTION OF A POWER CONVERTER FOR ENERGY STORAGE SYSTEM	3

4.1.	Operation	3

4.2.	General characteristics	4

4.3.	Environment	4

4.4.	Performances	5

5.	CONSTRUCTION SPECIFICATION	5

6.	USER INTERFACES, controls and alarms	5

7.	FACTORY TESTING AND INSPECTION	6

8.	COMMISSIONING	6

9.	MAINTENANCE CONTRACT	7

10.	WARRANTY	7

# ABBREVIATIONS

For the purpose of this document, we have used the following standard abbreviations:

PCS	Power converter

PMS	Power Management System

EMS	Energy Management System

ESS	Energy Storage System

HMI	Human Machine Interface

THDI	Total Harmonic Distortion in Current

EMC	Electro Magnetic Compatibility

IEC	International Electrotechnical Commission

EU	European Conformity

EN	European Norms

UL 	American Norms

# USER GUIDE

Paragraphs shown in red refer to options. They should be deleted if these options are not relevant to the current project. .

Notes shown in purple are intended for specification users (engineering consultants or Socomec spec engineers). Delete these notes before the specification is published.

# PURPOSE OF THE SPECIFICATION DOCUMENT

This specification document describes the power converter (PCS) used in energy storage installations.

The technical reference is SOCOMEC SUNSYS PCS² 33kVA, 66kVA, 100kVA or 200kVA of rated power.

# NORMATIVE COMPLIANCE

The PCS must comply with the following standards:

Keep the below texts for a product to be sold to the United States – Grid codes not for the 200kVA:

- Safety: 		UL 1741SA.

- EMC: 		FCC Part 15.

- Software:		UL 1998.

- Grid Code :		IEEE 1547-2003, IEEE 1547a-2014, IEEE 1547.1-2005

Keep the below texts for a product to be sold to Europe – Grid codes not for the 200kVA:

- Safety: 		EN 62477-1 and EN 60950-1/A2.

- EMC: 		EN 61000-3-12, EN 61000-6-2, EN 61000-6-3 and EN 61000-3-11 (33 to 100kVA)

EN 61000-6-2 and EN 61000-4 (200kVA)

- Grid Code :		VDE 0126-1-1/A1 (France)

VDE ARN 4105 (Germany)

CEI 0-21 (Italy)

CEI 0-16 (Italy)

# ORIGIN

The PCS must be developed, manufactured and tested in a European country (Italy). The development and production site must be certified according to ISO14001 (Environmental management system) and ISO9001 (Quality management system).

Keep the below texts for a product to be sold to Europe:

PCS covered by this specification must have the EU marking, in accordance with European directive on safety and electromagnetic:  2014/35/UE (Low voltage directive) and 2014/30/UE (EMC). Relevant documentation and certificates must be made available on request.

# GLOBAL DESCRIPTION OF A POWER CONVERTER FOR ENERGY STORAGE SYSTEM

# Operation

The PCS is an electronic system that converts AC electrical energy in DC or vice versa in order to charge or discharge batteries. It has to be composed of a single bidirectional conversion stage and equipped with an internal galvanic isolation between AC & DC connection points.

The galvanic isolation enables:

- To isolate DC side from AC side

- To prevent the injection of continuous current on the AC side

- To limit the impact of a DC isolation fault on the AC side.

The DC side has to be monitored to control the insulation in order to detect any earth fault.

The PCS also has to be based on a modular architecture in order to optimise its upgradability, its reliability, its life duration and its maintainability.

The PCS are composed of power modules that must have a rated power higher than 25kVA and lower than 35kVA. The total power of a PCS shouldn’t exceed a rated power of 200kVA.

These power modules must be hot swappable, without any impact on the operation of other modules of the conversion device, in less than 5 minutes.

The PCS have to be able to work in parallel up to 5 units (10 units up to 100kVA) using a dedicated Power Management System.

# General characteristics

| Apparent rated power | 33 kVA, 66kVA, 100 kVA or 200kVA |
| --- | --- |
| Active rated power (Pn) | 33 kW, 66kW, 100kW or 200 kW |
| Apparent rated power per module | 33 kVA |
| Active rated power per module (Pn) | 33 kW |
| DC operating voltage range | 450 to 825 VDC without derating 350 to 850 VDC with derating |
| Maximum discharging current per module | 80 A |
| Number of poles | 3 P |
| AC nominal voltage | 400 VAC (to be kept for CE – TR versions) 480 VAC (to be kept for UL – TR versions) 280 VAC (to be kept for TL versions) |
| AC operating voltage range | 320 to 480 VAC (to be kept for CE – TR versions) 423 to 528 VAC (to be kept for UL – TR versions) 252 to 308 VAC (to be kept for TL versions – except 200kVA CE) 224 to 336 VAC (to be kept for the 200kVA CE version) |
| Rated frequency | 50 Hz (to be kept for CE – TR versions) 60 Hz (to be kept for UL – TR versions) |
| Operating frequency range | 47.5 to 51.5 Hz (to be kept for CE – TR versions) 59.3 to 60.5 Hz (to be kept for UL – TR versions) |

# Environment

- Operating temperature range: 		from 0°C to + 40°C without derating (to be kept for CE versions)

from -5°C to + 50°C with derating (to be kept for CE versions)

from 32°F to 104°F without derating (to be kept for UL  versions)

from 23°F to 122°F with derating (to be kept for UL  versions)

- Storage temperature range: 		from -5°C to + 60°C (to be kept for CE versions)

from 23°F to 140°F (to be kept for UL  versions)

- Altitude, without derating: 		≤1000m (to be kept for CE versions)

≤3300ft (to be kept for UL  versions)

- Relative humidity: 			5% to 95 % at ambient temperature, without condensation

- Ingress protection:			IP 20 (to be kept for CE versions)

NEMA 1 (to be kept for UL versions)

- Acoustic noise at 1m: 			< 67 dB

# Performances

- THDI: 				<3%

- Efficiency: 				>95% from 15 kW.

To maximise the efficiency, the PCS has to be equipped with a wattmeter management system enabling it to operate with the just enough number of power modules according to the received order. Thus, the non-used modules stay in standby mode and the others can operate at their optimum.

- P/Q operation:	 			100%

The PCS has to be able to respect and follow orders in the entire P/Q diagram, which means 100% of Sn and this whatever the face (+C/-C/+L/-L)

- Response time:

To answer at best to operational constraints, it is important for the energy storage system to be able to follow precisely and quickly order modifications coming from an EMS or PMS.

- 0%	==>	+100% (Charge):			<35ms

- 0%  ==>	-100% (Discharge):			<35ms

- -100%  ==> 	+100% (Discharge/Charge):		<35ms

- +100%  ==> 	-100% (Charge/Discharge):		<35ms

# CONSTRUCTION SPECIFICATION

It will be mandatory, to install a PCS, to keep 30cm space at the back of the machine in a 40°C ambient temperature room:

- Connection of loads and batteries needs to be done from the bottom

- The PCS will be cooled with forces ventilation: the air inlet will be on the front panel and the outlet vent will be at the back of the cabinet

- Maintenance operations will be done via top access only and the preventive replacement of components will be eased to shorten the mean time to repair.

Each unit will be equipped with switches upstream and downstream: these will allow work on the electronics or power modules to be done in safety.

Shall the installation be equipped with an air exit system; the back space would be limited to 10cm for an ambient temperature of 40°.

# USER INTERFACES, controls and alarms

The user interface on the PCS must consist of a graphical colour display with the following features:

- Min 3.5" screen. High Definition (min. 320x240 pixels) with backlight;

- Display of PCS status, measurements and alarms

- Display of events historical

- Local configuration, supervision and control of the PCS

This HMI gives access to:

- Operating states: Local / Distant – On / Off – Charge / Discharge

- Instantaneous alarms and alerts of each modules

- Instantaneous power electrical values in kW

- State of charge of the batteries

- Configuration of the conversion unit parameters: system, network...

It must be possible to update the firmware simply and automatically by connecting a USB key in the HMI. The same process must enable the update of languages.

The PCS must be equipped with specific input terminals to enable an external emergency stop to activate, stop and disconnect the PCS by opening the DC and AC contactors.

# FACTORY TESTING AND INSPECTION

The supplier of the equipment must be able to offer factory acceptance tests and in the presence of the customer. All tests will be carried out with appropriate measuring instruments, their accuracy guaranteed by a certificate of calibration. Following the positive outcome of the test procedure, the manufacturer shall prepare a certificate listing the tests performed and the results obtained.

# COMMISSIONING

After installing the equipment and its power supply, commissioning will be carried out by technicians trained and certified by the PCS manufacturer.

The following steps must be performed:

- Visual inspection of the PCS and absence of intruding objects,

- Checking of electrical and mechanical connection of the PCS,

- Functional tests to check its operation,

- Validation of the measurements taken during factory tests,

- A complete charge and discharge cycle of the battery,

- Load-testing,

- Installation and verification of the transfer of data to the supervision station

- Basic training for system users :

- General description of how to use the system

- Instructions on use and maintenance

At the end of the commissioning procedure, the technician will need to create a full report on the work undertaken.

# MAINTENANCE CONTRACT

The PCS manufacturer must be able to ensure the maintenance of the installed equipment, by means of a maintenance contract. This should be done by technicians trained and certified by the manufacturer of the equipment. A secured remote connection will be required to access to the monitoring of the equipment.

# WARRANTY

The PCS warranty, against all failures, must be at least of 2 years.

It must be possible to offer a 5 or 10 years warranty extension as a contract.

The tests may be carried out only with the existing system load or a test load provided by the customer.