SECTION 26 ## ##

MULTI-CIRCUIT SUBMETERING

PART 1 – GENERAL

  - SUMMARY

- This specification describes a revenue grade, multi-channel submeter and associated millivolt current sensors by Socomec, allowing to monitor up to 16 three-phase circuits and report measurement data to an external EMS/BMS.

- The technical benchmark is SOCOMEC DIRIS MCM-48 and associated mV current sensors, or equal and approved.

- The DIRIS MCM48 is well-suited for datacenter multi-circuit monitoring, tenant sub metering, and for accountability metering in commercial, retail, and industrial facilities.

The following text is formatted for inclusion in an engineering consultant’s technical specifications.

PART 2 – PRODUCTS

  - MANUFACTURERS

  - Subject to compliance with requirements, provide products by one of the following:

- Revenue grade multi-channel power meter

- SOCOMEC DIRIS MCM-48

- …

  - MULTI-CHANNEL METER REQUIREMENTS

  - Meter shall monitor voltage, current, power, energy, and many other electrical parameters on an electrical system, including but not limited to:

    - System and Phase measurements for: Amps, Volts, Frequency, kW, kWh, KVAR, kVARh, kVA, kVAh, dPF or aPF.

    - Net System True Energy (kWh), Net System Apparent Energy (kVAh), Net System Reactive Energy (kVARh)

    - System True Power +/- (kW)

      - Meter shall be capable of measuring both positive and negative power to ascertain between power demand or power generation for demand response, smart grid and on-site generation applications.

    - System True Energy +/- (kWh), Apparent Energy +/- (kVAh) & four Quadrant Reactive Energy (kVARh)

      - Meter shall be capable of measuring both positive and negative energy to ascertain between energy consumption or energy generation for demand response, smart grid and on-site generation applications.

    - 15 Minute Peak Demand.

  - The meter shall be universally compatible with service voltages ranging from 90-277 VAC L-N, 480 VAC L-L, CAT III and shall not require the addition of a step down potential transformer.

  - The meter shall support all service types (Single-Phase Two-Wire Line-to-Neutral; Single-Phase Two-Wire Line-to-Line; Single-Phase Three-Wire (Split-Phase); Three- Phase Three-Wire DELTA; Three-Phase Four-Wire WYE).

  - Meter shall be Line-Powered from L1 Phase to L2 Phase. 90-480 VAC, CAT III, 50/60Hz, 500mA max.  No external power supplies shall be required to power the meter.

  - The meter shall monitor up to 16 three-phase circuits and allow to monitor a mix of three-phase, split-phase, and single-phase circuits, ranging from 0 – 6000 Amps.

  - Meter shall accept 0 to 0.333VAC current sensors and therefore permit connection and disconnection of current sensors under load without shorting blocks.

  - Current sensors shall come from the same manufacturer as the meter and shall be available in split-core configuration or Rogowski coil to simplify retrofit in existing installations

  - For busbar and high current applications, meter shall support Rogowski coil with 131mV/1000A @ 60Hz.

  - Current sensors shall be interchangeable on the meter.

  - The meter shall provide a clear visible numbering of CT inputs, with color-coded terminals that match the white/black CT lead wires. This ensures easy circuit identification and minimizes the risk of wiring errors.

  - The meter shall provide measurement data updates every 1 second.

  - Meter shall be available with Serial RS-485, Wireless (915 MHz), and Ethernet interface.

    - Serial RS-485 communication shall support Modbus RTU protocol using IEEE-754 single precision floating point.

    - Ethernet communication shall support Modbus TCP protocol using IEEE-754 single precision floating point.

    - Wireless communication shall support Modbus though the RS-485 port on the meter and shall not require a separate power supply.

  - Meter shall provide tri-color backlight through an LCD light pipe on top front of MCM 48.

  - Meter shall be equipped with a USB port for meter powering and configuring the device, even offline.

  - Meter shall include Interval Data Recording with a capacitor-backed real time clock. The meter shall have non-volatile memory to store up to 63 days of 15- minute interval kWh data for each CT channel.

  - The meter shall have 2 levels of PIN protection Security (Read/Write or Read-Only)

  - The meter shall provide a high voltage cover rated IP30 to prevent user-direct access to dangerous high voltages. This will keep instrumentation engineers safe when operating the meter while front cover is removed, even with live voltage.

  - The meter shall be equipped with internal fuse protection on each hot leg.

  - Meter shall comply with the following Safety Specification:

      - UL Listed

      - Conforms to UL Std 61010-1 3rd Ed

      - Certified to CSA Std C22.2 No. 61010-1 3rd Ed

  - Meter shall be revenue grade and accuracy with accuracy class 0.2 per ANSI C12.20 2010 or better.

  - Meter shall be capable of operating in ambient conditions ranging from –at least 4ºF to +140ºF (-20ºC to +60ºC).

  - Meter dimensions shall not exceed (L) 521 mm x (W) 277 mm x (H) 89 mm (20.5” x 10.9” x 3.1”)

  - High voltage cover is rated IP30.

PART 3 – EXECUTION

3.01	INSTALLATION

- Preparation shall be in accordance with reviewed product data, final shop drawing and manufacturer’s recommendations.

- Installation shall be in accordance with manufacturer’s instructions.

- Identify components according to Division 26 section “Identification for Electrical Systems”.

3.02	CONNECTION

- Wiring connection shall be in accordance with manufacturer’s instructions.

- Wiring connection shall be according to Division 26 section “Low-Voltage Electrical Power Conductors and cables”.

3.03      COMMISSIONING

The manufacturer shall propose optional remote and on-site commissioning services for the power meter and visualization software.

3.03	MAINTENANCE & TRAINING

- Operation and Maintenance Instruction: Personnel shall be formally trained by the manufacturer’s authorized representative as to the proper operation and maintenance of the power meter.

3.04	TESTING

- The power meter shall be declared conform to the UL standards by a testing laboratory having the NRTL (National Recognized Testing Laboratory) qualification.

- After installing equipment, execute test reports in accordance with manufacturer’s instructions.

END OF SECTION