DIRIS MCM SUBMETER AND ASSOCIATED MILLIVOLT OUTPUT CURRENT SENSORS BY SOCOMEC.

PROVIDE DIRIS MCM-16 WITH 16 CURRENT SENSOR INPUTS TO MONITOR UP TO 5 THREE-PHASE CIRCUITS OR A MIX OF SINGLE-PHASE, SPLIT-PHASE AND THREE-PHASE CIRCUITS.

PROVIDE DIRIS MCM-48 WITH 48 CURRENT SENSOR INPUTS TO MONITOR UP TO 16 THREE-PHASE CIRCUITS OR A MIX OF SINGLE-PHASE, SPLIT-PHASE AND THREE-PHASE CIRCUITS.

METER SHALL ALLOW TO MONITOR DIFFERENT LOAD CATEGORIES IN ACCORDANCE WITH ASHRAE 90.1 2019 REQUIREMENTS AND IECC 2021 ENERGY CODE.

METER ENCLOSURE SHALL INCLUDE NATIVE 1-IN CONDUIT HOLES TO FACILITATE FASTER INSTALLATION.

METER SHALL BE UNIVERSALLY COMPATIBLE WITH ALL SERVICE TYPES AND VOLTAGES UP TO 600 VAC AND SHALL BE LINE POWERED.

METER SHALL INCLUDE DUAL VOLTAGE MONITORING FOR ADDITIONAL VOLTAGE LINE SYSTEMS FROM 90 VAC to 250 VAC MEASUREMENTS.

METER SHALL INCLUDE NATIVE DISCONNECT SWITCH TO BE ABLE TO SERVICE THE METER INDEPENDANTLY OF OTHER CIRCUITS.

METER SHALL INCLUDE LOCAL DISPLAY FOR LOCAL VISUZALISATION OF MEASUREMENTS.

METER SHALL REPORT MEASUREMENT DATA VIA RS485 MODBUS RTU, ETHERNET MODBUS TCP AND BACNET IP COMMUNICATION FOR EASY INTEGRATION TO CLIENT EMS/BMS.

METER SHALL INCLUDE OPERATION ENVIRONMENTAL RATINGS FROM -4 to +140 °F / -20 to +60°C WITHOUT DERATING.