## ATYS_g_M_tri
|  |  | Config | [8 empty] | Initial state |  |  |  |  | Event1 |  | State1 |  |  |  |  | Event2 |  | State2 |  |  |  |  | Event3 |  | State3
Test case | Enable ? | Comments or test case description | Mode | Network | Network Application | InputFct1 | InputFct2 | InputFct3 | Stop in 0 ? | RT (s) | FT (s) | S1 available ? | S2 available ? | Position | GenSet | Product Availability | Description | Post-event timer (s) | S1 available ? | S2 available ? | Position | GenSet | Product Availability | Description | Post-event timer (s) | S1 available ? | S2 available ? | Position | GenSet | Product Availability | Description | Post-event timer (s) | S1 available ? | S2 available ? | Position | GenSet | Product Availability
10 | Yes | Basic in M/G: loss of S1, check that StartGen becomes ON and then that the product goes to P2 | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | No | 1 | No check | ON | (1) Turn off Source 1 | 6 | No | No | 1 | ON | OFF | (4) Turn on Source 2 | 8 | No | Yes | 2 | ON | ON
11 | Yes | Idem case 10 but not all 3 phases of S1 are lost, only one | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | No | 1 | No check | ON | (5) Lose one phase of Source 1 | 6 | Yes | No | 1 | ON | ON | (4) Turn on Source 2 | 8 | Yes | Yes | 2 | ON | ON
12 | No | Idem case 10 but in 1P+N network mode | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | No | 1 | No check | ON | (1) Turn off Source 1 | 6 | No | No | 1 | ON | OFF | (4) Turn on Source 2 | 6 | No | Yes | 2 | ON | ON
20 | Yes | Test come back in P1 when S1 returns | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 1 | ON | ON
22 | No | Idem case 20 but in 1P+N network mode | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (3) Turn on Source 1 | 8 | Yes | Yes | 1 | ON | ON
30 | Yes | Loss of S1, StartGen ON but S1 comes back : check StartGen shuts immediatly OFF and product is still in P1 | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | No | 1 | No check | ON | (1) Turn off Source 1 | 6 | No | No | 1 | ON | OFF | (3) Turn on Source 1 | 8 | Yes | No | 1 | OFF | ON
32 | No | Idem case 30 but in 1P+N network mode | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | No | 1 | No check | ON | (1) Turn off Source 1 | 6 | No | No | 1 | ON | OFF | (3) Turn on Source 1 | 8 | Yes | No | 1 | OFF | ON
80 | Yes | Product in P2 with only S2 available, manual retransfert mode, then S1 comes back but check that product stays in P2 | Auto | 3P+N | M/G | (C) Manual retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | no | Yes | 2 | ON | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | ON | ON | (1) Turn off Source 1 | 6 | No | Yes | 2 | ON | ON
82 | No | Idem case 80 but in 1P+N network mode | Auto | 1P+N | M/G | (C) Manual retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (3) Turn on Source 1 | 8 | Yes | Yes | 2 | ON | ON | (1) Turn off Source 1 | 3 | No | Yes | 2 | ON | ON
100 | Yes | Gen already available when loss S1, product goes directly to P2 | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | No check | ON | (1) Turn off Source 1 | 6 | No | Yes | 2 | ON | ON
110 | Yes | Loss of S1 but no start of the Gen S2 : check product stays in P1 and no more available | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | No | 1 | No check | ON | (1) Turn off Source 1 | 6 | No | No | 1 | ON | OFF
110 | No | Idem case 110 but in 1P+N network mode | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | No | 1 | No check | ON | (1) Turn off Source 1 | 6 | No | No | 1 | ON | OFF
180 | Yes | Product in P2 with only S2 available, loss of S2 : check that product still in P2 but no more available | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (2) Turn off Source 2 | 6 | No | No | 2 | ON | OFF
182 | No | Idem case 180 but in 1P+N network mode | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (2) Turn off Source 2 | 6 | No | No | 2 | ON | OFF
190 | Yes | Idem case 180 but then S2 comes back : check product is available again in P2 | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (2) Turn off Source 2 | 6 | No | No | 2 | ON | OFF | (4) Turn on Source 2 | 8 | No | Yes | 2 | ON | ON
192 | No | Idem case 190 but in 1P+N network mode | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (2) Turn off Source 2 | 6 | No | No | 2 | ON | OFF | (4) Turn on Source 2 | 8 | No | Yes | 2 | ON | ON
200 | Yes | Idem case 180 but then S1 comes back : check product is available again but in P1 and StartGen OFF | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (2) Turn off Source 2 | 6 | No | No | 2 | ON | OFF | (3) Turn on Source 1 | 8 | Yes | No | 1 | OFF | ON
202 | No | Idem case 200 but in 1P+N network mode | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (2) Turn off Source 2 | 6 | No | No | 2 | ON | OFF | (3) Turn on Source 1 | 8 | Yes | No | 1 | OFF | ON
210 | Yes | Both S1 and S2 available, product in P1, loss of S2 : check StartGen is still OFF, product vailable in P1 | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | No check | ON | (2) Turn off Source 2 | 6 | Yes | No | 1 | OFF | ON
212 | No | Idem case 210 but in 1P+N network mode | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | No check | ON | (2) Turn off Source 2 | 6 | Yes | No | 1 | OFF | ON
240 | Yes | Product in P2 with only S2 available, then inhibit auto mode : check that product is no more available, and then return to initial state | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (8) Toggle state of inhibit auto option | 6 | No | Yes | 2 | ON | OFF | (8) Toggle state of inhibit auto option | 6 | No | Yes | 2 | ON | ON
242 | No | Idem case 240 but in 1P+N network mode | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (8) Toggle state of inhibit auto option | 6 | No | Yes | 2 | ON | OFF | (8) Toggle state of inhibit auto option | 6 | No | Yes | 2 | ON | ON
250 | Yes | Product in P2 with only S2 available, then inhibit auto mode and S1 comes back : check that product stays in P2 | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (8) Toggle state of inhibit auto option | 6 | No | Yes | 2 | ON | OFF | (3) Turn on Source 1 | 8 | Yes | Yes | 2 | ON | OFF
252 | No | Idem case 250 but in 1P+N network mode | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (8) Toggle state of inhibit auto option | 6 | No | Yes | 2 | ON | OFF | (3) Turn on Source 1 | 8 | Yes | Yes | 2 | ON | OFF
260 | Yes | Idem case 250 but then enable again auto mode and check that the products switches to P1 | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (8) Toggle state of inhibit auto option | 6 | No | Yes | 2 | ON | OFF | (3) Turn on Source 1 | 8 | Yes | Yes | 2 | ON | OFF | (8) Toggle state of inhibit auto option | 245 | Yes | Yes | 1 | OFF | ON
262 | No | Idem case 260 but in 1P+N network mode | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (8) Toggle state of inhibit auto option | 6 | No | Yes | 2 | ON | OFF | (3) Turn on Source 1 | 8 | Yes | Yes | 2 | ON | OFF | (8) Toggle state of inhibit auto option | 245 | Yes | Yes | 1 | OFF | ON
380 | Yes | Test on load : starts in P1, check that StartGen becomes ON, go to P2 | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | No | 1 | No check | ON | (11) Toggle state of on load test option | 10 | Yes | No | 1 | ON | ON | (4) Turn on Source 2 | 10 | Yes | Yes | 2 | ON | ON
382 | No | Idem case 380 but in 1P+N network mode | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | No | 1 | No check | ON | (11) Toggle state of on load test option | 10 | Yes | No | 1 | ON | ON | (4) Turn on Source 2 | 10 | Yes | Yes | 2 | ON | ON
420 | Yes | Test on load as case 380 but with loss of S1 | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | No check | ON | (11) Toggle state of on load test option | 15 | Yes | Yes | 2 | ON | ON | (1) Turn off Source 1 | 6 | No | Yes | 2 | ON | ON
430 | Yes | Idem case 420 but then S1 comes back | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | No check | ON | (11) Toggle state of on load test option | 15 | Yes | Yes | 2 | ON | ON | (1) Turn off Source 1 | 6 | No | Yes | 2 | ON | ON | (3) Turn on Source 1 | 5 | Yes | Yes | 2 | ON | ON
440 | Yes | Idem case 380 but then inhibit auto mode and disable test on load : check that the product stays in P2 | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | No check | ON | (11) Toggle state of on load test option | 15 | Yes | Yes | 2 | ON | ON | (8) Toggle state of inhibit auto option | 6 | Yes | Yes | 2 | ON | OFF | (11) Toggle state of on load test option | 5 | Yes | Yes | 2 | ON | OFF
442 | No | Idem case 440 but in 1P+N network mode | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | No check | ON | (11) Toggle state of on load test option | 15 | Yes | Yes | 2 | ON | ON | (8) Toggle state of inhibit auto option | 6 | Yes | Yes | 2 | ON | OFF | (11) Toggle state of on load test option | 5 | Yes | Yes | 2 | ON | OFF
470 | Yes | Test on load and then disable it : check product comes back in P1 | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | No check | ON | (11) Toggle state of on load test option | 15 | Yes | Yes | 2 | ON | ON | (11) Toggle state of on load test option | 10 | Yes | Yes | 1 | ON | ON
472 | No | Idem case 470 but in 1P+N network mode | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | No check | ON | (11) Toggle state of on load test option | 15 | Yes | Yes | 2 | ON | ON | (11) Toggle state of on load test option | 10 | Yes | Yes | 1 | ON | ON
480 | Yes | Inhibit auto mode and then start test on load : check that product stays in S1 | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | No | 1 | No check | ON | (8) Toggle state of inhibit auto option | 6 | Yes | No | 1 | No check | OFF | (11) Toggle state of on load test option | 6 | Yes | No | 1 | No check | OFF
482 | No | Idem case 480 but in 1P+N network mode | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | No | 1 | No check | ON | (8) Toggle state of inhibit auto option | 6 | Yes | No | 1 | No check | OFF | (11) Toggle state of on load test option | 6 | Yes | No | 1 | No check | OFF
520 | Yes | Loss of S1 with manual retransfert mode enabled, turn on S2 and check that the product goes to P2 | Auto | 3P+N | M/G | (C) Manual retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | No | 1 | No check | ON | (1) Turn off Source 1 | 6 | No | No | 1 | ON | OFF | (4) Turn on Source 2 | 8 | No | Yes | 2 | ON | ON
522 | No | Idem case 520 but in 1P+N network mode | Auto | 1P+N | M/G | (C) Manual retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | No | 1 | No check | ON | (1) Turn off Source 1 | 6 | No | No | 1 | ON | OFF | (4) Turn on Source 2 | 8 | No | Yes | 2 | ON | ON
550 | Yes | Product is in P2 with both S1 and S2 available, with manual retransfert mode enabled, then disabled this mode and check that product comes back to P1 | Auto | 3P+N | M/G | (C) Manual retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (3) Turn on Source 1 | 8 | Yes | Yes | 2 | ON | ON | (7) Toggle state of retransfer option | 245 | Yes | Yes | 1 | OFF | ON
551 | Yes | Product is in P2 with both S1 and S2 available, with manual retransfert mode enabled, then loss of S2 and check that product comes back to P1 | Auto | 3P+N | M/G | (C) Manual retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (3) Turn on Source 1 | 8 | Yes | Yes | 2 | ON | ON | (2) Turn off Source 2 | 10 | Yes | No | 1 | OFF | ON
552 | No | Idem case 550 but in 1P+N network mode | Auto | 1P+N | M/G | (C) Manual retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (3) Turn on Source 1 | 8 | Yes | Yes | 2 | ON | ON | (7) Toggle state of retransfer option | 245 | Yes | Yes | 1 | OFF | ON
600 | Yes | Product in P2, S1 comes back, check that product comes back to P1 and then wait to test cooldown timer (240 s after main returns, StartGen must stop) | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 1 | ON | ON | (0) No event | 245 | Yes | Yes | 1 | OFF | ON
602 | No | Idem case 600 but in 1P+N network mode | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 1 | ON | ON | (0) No event | 245 | Yes | Yes | 1 | OFF | ON
810 | No | Product in manual mode, in P1 with only S1 available, then S1 is lost but product doesn't switch to P2 | Manual | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | No | 1 | No check | OFF | (1) Turn off Source 1 | 15 | No | No | 1 | No check | OFF
812 | No | Idem case 810 but in 1P+N network mode | Manual | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | No | 1 | No check | OFF | (1) Turn off Source 1 | 15 | No | No | 1 | No check | OFF
820 | No | Product in manual mode, in P1 with both S1 and S2 available, then S2 is lost | Manual | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | No check | OFF | (2) Turn off Source 2 | 6 | Yes | No | 1 | No check | OFF
822 | No | Idem case 820 but in 1P+N network mode | Manual | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | No check | OFF | (2) Turn off Source 2 | 6 | Yes | No | 1 | No check | OFF
1070 | No | No source available, product in P1 and manual mode. Then S1 comes back | Manual | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | No | 1 | No check | OFF | (3) Turn on Source 1 | 8 | Yes | No | 1 | No check | OFF
1072 | No | Idem case 1070 but in 1P+N network mode | Manual | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | No | 1 | No check | OFF | (3) Turn on Source 1 | 8 | Yes | No | 1 | No check | OFF
1080 | No | No source available, product in P1 and manual mode. Then S2 comes back but product doesn't switch to P2 | Manual | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | No | 1 | No check | OFF | (4) Turn on Source 2 | 8 | No | Yes | 1 | No check | OFF
1082 | No | Idem case 1080 but in 1P+N network mode | Manual | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | No | 1 | No check | OFF | (4) Turn on Source 2 | 8 | No | Yes | 1 | No check | OFF
1110 | No | No source available, product in P0 and manual mode. Then S1 comes back but product doesn't switch to P1 | Manual | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | No | 0 | No check | OFF | (3) Turn on Source 1 | 8 | Yes | No | 0 | No check | OFF
1112 | No | Idem case 1110 but in 1P+N network mode | Manual | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | No | 0 | No check | OFF | (3) Turn on Source 1 | 8 | Yes | No | 0 | No check | OFF
1120 | No | No source available, product in P0 and manual mode. Then S2 comes back but product doesn't switch to P2 | Manual | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | No | 0 | No check | OFF | (4) Turn on Source 2 | 8 | No | Yes | 0 | No check | OFF
1122 | No | Idem case 1120 but in 1P+N network mode | Manual | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | No | 0 | No check | OFF | (4) Turn on Source 2 | 8 | No | Yes | 0 | No check | OFF
1150 | No | No source available, product in P2 and manual mode. Then S1 comes back but product doesn't switch to P1 | Manual | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | No | 2 | No check | OFF | (3) Turn on Source 1 | 8 | Yes | No | 2 | No check | OFF
1152 | No | Idem case 1150 but in 1P+N network mode | Manual | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | No | 2 | No check | OFF | (3) Turn on Source 1 | 8 | Yes | No | 2 | No check | OFF
1160 | No | No source available, product in P2 and manual mode. Then S2 comes back | Manual | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | No | 2 | No check | OFF | (4) Turn on Source 2 | 8 | No | Yes | 2 | No check | OFF
1162 | No | Idem case 1160 but in 1P+N network mode | Manual | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | No | 2 | No check | OFF | (4) Turn on Source 2 | 8 | No | Yes | 2 | No check | OFF
1170 | No | Loss of S1, check that StartGen becomes ON but then open front control panel : the product doesn't switch to P2 | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | No | 1 | No check | ON | (1) Turn off Source 1 | 6 | No | No | 1 | ON | OFF | (12) Manually open front control panel | 5 | No | Yes | 1 | ON | OFF | (4) Turn on Source 2 | 8 | No | Yes | 1 | ON | OFF
1172 | No | Idem case 1170 but in 1P+N network mode | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | No | 1 | No check | ON | (1) Turn off Source 1 | 6 | No | No | 1 | ON | OFF | (12) Manually open front control panel | 5 | No | Yes | 1 | ON | OFF | (4) Turn on Source 2 | 8 | No | Yes | 1 | ON | OFF
2000 | No | Reference test for fail timer in M/G mode : loss of S1, check that StartGen is ON and that product goes directly to P2 | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | No | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | No | 1 | ON | OFF
2001 | No | Idem case 2000 but with fail timer test to 5s | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 5 | Yes | No | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | No | 1 | OFF | OFF | (0) No event | 5 | No | No | 1 | ON | OFF
2002 | No | Idem case 2000 but with fail timer test to 20s | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 20 | Yes | No | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | No | 1 | OFF | OFF | (0) No event | 25 | No | No | 1 | ON | OFF
2003 | No | Idem case 2000 but with fail timer test to 60s | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 60 | Yes | No | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | No | 1 | OFF | OFF | (0) No event | 65 | No | No | 1 | ON | OFF
2004 | No | 05.23 : not passed !! Idem case 2003 but S1 state toggles 5 times during fail timer, to check if product ignore this non-significant return of main power supply and goes to P2 anyway | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 60 | Yes | No | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | No | 1 | OFF | OFF | (14) Rapid toggle of Source 1 state 5x | 65 | No | No | 1 | ON | OFF
2005 | No | Idem case 2003 but S1 comes back before end of fail timer, to check if product stays in P1 and StartGen OFF | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 60 | Yes | No | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | No | 1 | OFF | OFF | (3) Turn on Source 1 | 5 | Yes | No | 1 | OFF | ON
2006 | No | Reference test for return timer in M/G mode : product in P2, S1 comes back and check that product comes back to P1 | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (3) Turn on Source 1 | 10 | Yes | Yes | 1 | ON | ON
2007 | No | Idem case 2006 but with return timer test to 3 min | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 180 | 0 | No | Yes | 2 | ON | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | ON | ON | (0) No event | 185 | Yes | Yes | 1 | ON | ON
2008 | No | Idem case 2007 but S1 state toggles 5 times during return timer, to check if product ignore non-significant failures of main power supply and switches to P1 anyway | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 180 | 0 | No | Yes | 2 | ON | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | ON | ON | (14) Rapid toggle of Source 1 state 5x | 185 | Yes | Yes | 1 | ON | ON
2009 | No | Idem case 2006 but with return timer test to 10 min | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 600 | 0 | No | Yes | 2 | ON | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | ON | ON | (0) No event | 605 | Yes | Yes | 1 | ON | ON
2010 | No | Idem case 2006 but with return timer test to 30 min | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 1800 | 0 | No | Yes | 2 | ON | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | ON | ON | (0) No event | 1805 | Yes | Yes | 1 | ON | ON
2100 | No | Idem case 2000 but in 1P+N network mode | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | No | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | No | 1 | ON | OFF
2101 | No | Idem case 2100 but with fail timer test to 5s | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 5 | Yes | No | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | No | 1 | OFF | OFF | (0) No event | 5 | No | No | 1 | ON | OFF
2102 | No | Idem case 2100 but with fail timer test to 20s | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 20 | Yes | No | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | No | 1 | OFF | OFF | (0) No event | 25 | No | No | 1 | ON | OFF
2103 | No | Idem case 2100 but with fail timer test to 60s | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 60 | Yes | No | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | No | 1 | OFF | OFF | (0) No event | 65 | No | No | 1 | ON | OFF
2104 | No | Idem case 2103 but S1 state toggles 5 times during fail timer, to check if product ignore this non-significant return of main power supply and goes to P2 anyway | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 60 | Yes | No | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | No | 1 | OFF | OFF | (14) Rapid toggle of Source 1 state 5x | 65 | No | No | 1 | ON | OFF
2105 | No | Idem case 2103 but S1 comes back before end of fail timer, to check if product stays in P1 and StartGen OFF | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 60 | Yes | No | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | No | 1 | OFF | OFF | (3) Turn on Source 1 | 5 | Yes | No | 1 | OFF | ON
2106 | No | Idem case 2006 but in 1P+N network mode | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (3) Turn on Source 1 | 10 | Yes | Yes | 1 | ON | ON
2107 | No | Idem case 2106 but with return timer test to 3 min | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 180 | 0 | No | Yes | 2 | ON | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | ON | ON | (0) No event | 185 | Yes | Yes | 1 | ON | ON
2108 | No | Idem case 2107 but S1 state toggles 5 times during return timer, to check if product ignore non-significant failures of main power supply and switches to P1 anyway | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 180 | 0 | No | Yes | 2 | ON | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | ON | ON | (14) Rapid toggle of Source 1 state 5x | 185 | Yes | Yes | 1 | ON | ON
2109 | No | Idem case 2106 but with return timer test to 10 min | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 600 | 0 | No | Yes | 2 | ON | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | ON | ON | (0) No event | 605 | Yes | Yes | 1 | ON | ON
2110 | No | Idem case 2106 but with return timer test to 30 min | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 1800 | 0 | No | Yes | 2 | ON | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | ON | ON | (0) No event | 1805 | Yes | Yes | 1 | ON | ON
2011 | No | Reference test for fail timer in M/M mode: loss of S1 with S2 available, check that the product switches directly to P2 | Auto | 3P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | Yes | 2 | OFF | ON
2012 | No | Idem case 2011 but with fail timer test to 5s | Auto | 3P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 5 | Yes | Yes | 1 | OFF | ON | (1) Turn off Source 1 | 8 | No | Yes | 2 | OFF | ON | (0) No event | 5 | No | Yes | 2 | OFF | ON
2013 | No | Idem case 2011 but with fail timer test to 20s | Auto | 3P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 20 | Yes | Yes | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | Yes | 1 | OFF | ON | (0) No event | 25 | No | Yes | 2 | OFF | ON
2014 | No | Idem case 2011 but with fail timer test to 60s | Auto | 3P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 60 | Yes | Yes | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | Yes | 1 | OFF | ON | (0) No event | 65 | No | Yes | 2 | OFF | ON
2015 | No | Idem case 2013 but S1 state toggles 5 times during fail timer, to check if product ignore this non-significant return of main power supply and goes to P2 anyway | Auto | 3P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 60 | Yes | Yes | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | Yes | 1 | OFF | ON | (14) Rapid toggle of Source 1 state 5x | 65 | No | Yes | 2 | OFF | ON
2016 | No | Idem case 2013 but S1 comes back before end of fail timer, to check if product stays in P1 and StartGen OFF | Auto | 3P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 60 | Yes | Yes | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | Yes | 1 | OFF | ON | (3) Turn on Source 1 | 5 | Yes | Yes | 1 | OFF | ON
2017 | No | Reference test for return timer in M/M mode: product in P2, S1 comes back and check that product comes back to P1 | Auto | 3P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | No | Yes | 2 | OFF | ON | (3) Turn on Source 1 | 10 | Yes | Yes | 1 | OFF | ON | [5 empty] | OFF
2018 | No | Idem case 2017 but with return timer test to 3 min | Auto | 3P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 180 | 0 | No | Yes | 2 | OFF | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | OFF | ON | (0) No event | 185 | Yes | Yes | 1 | OFF | ON
2019 | No | Idem case 2018 but S1 state toggles 5 times during return timer, to check if product ignore non-significant failures of main power supply and switches to P1 anyway | Auto | 3P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 180 | 0 | No | Yes | 2 | OFF | ON | (3) Turn on Source 1 | 6 | Yes | No | 2 | OFF | ON | (14) Rapid toggle of Source 1 state 5x | 185 | Yes | No | 1 | OFF | ON
2020 | No | Idem case 2017 but with return timer test to 10 min | Auto | 3P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 600 | 0 | No | Yes | 2 | OFF | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | OFF | ON | (0) No event | 605 | Yes | Yes | 1 | OFF | ON
2021 | No | Idem case 2017 but with return timer test to 30 min | Auto | 3P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 1800 | 0 | No | Yes | 2 | OFF | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | OFF | ON | (0) No event | 1805 | Yes | Yes | 1 | OFF | ON
2111 | No | Idem case 2011 but in 1P+N network mode | Auto | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | Yes | 2 | OFF | ON
2112 | No | Idem case 2111 but with fail timer test to 5s | Auto | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 5 | Yes | Yes | 1 | OFF | ON | (1) Turn off Source 1 | 8 | No | Yes | 2 | OFF | ON | (0) No event | 5 | No | Yes | 2 | OFF | ON
2113 | No | Idem case 2111 but with fail timer test to 20s | Auto | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 20 | Yes | Yes | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | Yes | 1 | OFF | ON | (0) No event | 25 | No | Yes | 2 | OFF | ON
2114 | No | Idem case 2111 but with fail timer test to 60s | Auto | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 60 | Yes | Yes | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | Yes | 1 | OFF | ON | (0) No event | 65 | No | Yes | 2 | OFF | ON
2115 | No | Idem case 2113 but S1 state toggles 5 times during fail timer, to check if product ignore this non-significant return of main power supply and goes to P2 anyway | Auto | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 60 | Yes | Yes | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | Yes | 1 | OFF | ON | (14) Rapid toggle of Source 1 state 5x | 65 | No | Yes | 2 | OFF | ON
2116 | No | Idem case 2113 but S1 comes back before end of fail timer, to check if product stays in P1 and StartGen OFF | Auto | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 60 | Yes | Yes | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | Yes | 1 | OFF | ON | (3) Turn on Source 1 | 5 | Yes | Yes | 1 | OFF | ON
2117 | No | Idem case 2017 but in 1P+N network mode | Auto | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | No | Yes | 2 | OFF | ON | (3) Turn on Source 1 | 10 | Yes | Yes | 1 | OFF | ON | [5 empty] | OFF
2118 | No | Idem case 2117 but with return timer test to 3 min | Auto | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 180 | 0 | No | Yes | 2 | OFF | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | OFF | ON | (0) No event | 185 | Yes | Yes | 1 | OFF | ON
2119 | No | Idem case 2118 but S1 state toggles 5 times during return timer, to check if product ignore non-significant failures of main power supply and switches to P1 anyway | Auto | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 180 | 0 | No | Yes | 2 | OFF | ON | (3) Turn on Source 1 | 6 | Yes | No | 2 | OFF | ON | (14) Rapid toggle of Source 1 state 5x | 185 | Yes | No | 1 | OFF | ON
2020 | No | Idem case 2117 but with return timer test to 10 min | Auto | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 600 | 0 | No | Yes | 2 | OFF | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | OFF | ON | (0) No event | 605 | Yes | Yes | 1 | OFF | ON
2021 | No | Idem case 2117 but with return timer test to 30 min | Auto | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 1800 | 0 | No | Yes | 2 | OFF | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | OFF | ON | (0) No event | 1805 | Yes | Yes | 1 | OFF | ON
3000 | No | Basic in M/M: loss of S1 with S2 available, check that the product goes to P2 | Auto | 3P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | OFF | ON | (1) Turn off Source 1 | 8 | No | Yes | 2 | OFF | ON
3001 | No | Idem case 3000 but not all 3 phases of S1 are lost, only one | Auto | 3P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | OFF | ON | (5) Lose one phase of Source 1 | 6 | Yes | Yes | 2 | OFF | ON
3002 | No | Idem case 3000 but in 1P+N network mode | Auto | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | Yes | 2 | OFF | ON
3020 | No | Product in P2 with only S2 available, then loss of S2, S1 comes back | Auto | 3P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | No | Yes | 2 | OFF | ON | (2) Turn off Source 2 | 6 | No | No | 2 | OFF | OFF | (3) Turn on Source 1 | 6 | Yes | No | 1 | OFF | ON
3022 | No | Idem case 3020 but in 1P+N network mode | Auto | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | No | Yes | 2 | OFF | ON | (2) Turn off Source 2 | 6 | No | No | 2 | OFF | OFF | (3) Turn on Source 1 | 6 | Yes | No | 1 | OFF | ON
3040 | No | With priority on S2, both S1 and S2 available, loss of S2 : the product must switch to P1 and then S2 comes back : the product must switch again to P2 | Auto | 3P+N | M/M | (O) Priority enabled | (C) Prio Source 2 | (O) Auto | No | 0 | 0 | Yes | Yes | 2 | OFF | ON | (2) Turn off Source 2 | 8 | Yes | No | 1 | OFF | ON | (4) Turn on Source 2 | 10 | Yes | Yes | 2 | OFF | ON
3041 | No | Idem case 3040 but not all 3 phases of S2 are lost, only one | Auto | 3P+N | M/M | (O) Priority enabled | (C) Prio Source 2 | (O) Auto | No | 0 | 0 | Yes | Yes | 2 | OFF | ON | (6) Lose one phase of Source 2 | 8 | Yes | Yes | 1 | OFF | ON
3042 | No | Idem case 3040 but in 1P+N network mode | Auto | 1P+N | M/M | (O) Priority enabled | (C) Prio Source 2 | (O) Auto | No | 0 | 0 | Yes | Yes | 2 | OFF | ON | (2) Turn off Source 2 | 8 | Yes | No | 1 | OFF | ON | (4) Turn on Source 2 | 10 | Yes | Yes | 2 | OFF | ON
3050 | No | Both S1 and S2 available, priority set to S1, then toggle priority to S2 : the product must switch to P2 | Auto | 3P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | OFF | ON | (10) Toggle priority source | 10 | Yes | Yes | 2 | OFF | ON
3052 | No | Idem case 3050 but in 1P+N network mode | Auto | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | OFF | ON | (10) Toggle priority source | 10 | Yes | Yes | 2 | OFF | ON
3060 | No | Product in P2, S2 only available. Change priority to S1, and then S1 comes back but product must stays in P2 | Auto | 3P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | No | Yes | 2 | OFF | ON | (9) Toggle state of priority enable option | 6 | No | Yes | 2 | OFF | ON | (3) Turn on Source 1 | 10 | Yes | Yes | 2 | OFF | ON
3062 | No | Idem case 3060 but in 1P+N network mode | Auto | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | No | Yes | 2 | OFF | ON | (9) Toggle state of priority enable option | 6 | No | Yes | 2 | OFF | ON | (3) Turn on Source 1 | 10 | Yes | Yes | 2 | OFF | ON
3070 | No | Set priority to S2 but disable priority with input 1. Product is in P1, S2 comes back but produt stays in P1 | Auto | 3P+N | M/M | (C) Priority disabled | (C) Prio Source 2 | (O) Auto | No | 0 | 0 | Yes | No | 1 | OFF | ON | (4) Turn on Source 2 | 6 | Yes | Yes | 1 | OFF | ON
3072 | No | Idem case 3070 but in 1P+N network mode | Auto | 1P+N | M/M | (C) Priority disabled | (C) Prio Source 2 | (O) Auto | No | 0 | 0 | Yes | No | 1 | OFF | ON | (4) Turn on Source 2 | 6 | Yes | Yes | 1 | OFF | ON
3080 | No | Set priority to S1 but disable priority with input 1. Product is in P2, S1 comes back but produt stays in P2 | Auto | 3P+N | M/M | (C) Priority disabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | No | Yes | 2 | OFF | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | OFF | ON
3082 | No | Idem case 3080 but in 1P+N network mode | Auto | 1P+N | M/M | (C) Priority disabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | No | Yes | 2 | OFF | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | OFF | ON
3090 | No | Product in P2, S2 only available. Inhibit auto mode, then S1 comes back, S2 is lost but product stays in P2 | Auto | 3P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | No | Yes | 2 | OFF | ON | (8) Toggle state of inhibit auto option | 6 | No | Yes | 2 | OFF | OFF | (3) Turn on Source 1 | 3 | Yes | Yes | 2 | OFF | OFF | (2) Turn off Source 2 | 3 | Yes | No | 2 | OFF | OFF
3092 | No | Idem case 3090 but in 1P+N network mode | Auto | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | No | Yes | 2 | OFF | ON | (8) Toggle state of inhibit auto option | 6 | No | Yes | 2 | OFF | OFF | (3) Turn on Source 1 | 3 | Yes | Yes | 2 | OFF | OFF | (2) Turn off Source 2 | 3 | Yes | No | 2 | OFF | OFF
3100 | No | Product in P1, S1 only available and priority is set to S2. Inhibit auto mode, then S2 comes back, S1 is lost but product stays in P1 | Auto | 3P+N | M/M | (O) Priority enabled | (C) Prio Source 2 | (O) Auto | No | 0 | 0 | Yes | No | 1 | OFF | ON | (8) Toggle state of inhibit auto option | 6 | Yes | No | 1 | OFF | OFF | (4) Turn on Source 2 | 3 | Yes | Yes | 1 | OFF | OFF | (1) Turn off Source 1 | 3 | No | Yes | 1 | OFF | OFF
3102 | No | Idem case 3100 but in 1P+N network mode | Auto | 1P+N | M/M | (O) Priority enabled | (C) Prio Source 2 | (O) Auto | No | 0 | 0 | Yes | No | 1 | OFF | ON | (8) Toggle state of inhibit auto option | 6 | Yes | No | 1 | OFF | OFF | (4) Turn on Source 2 | 3 | Yes | Yes | 1 | OFF | OFF | (1) Turn off Source 1 | 3 | No | Yes | 1 | OFF | OFF
3810 | No | Product in manual mode, product in P1 with both S1 and S2 available, loss of S1 but product stays in P1 | Manual | 3P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | OFF | OFF | (1) Turn off Source 1 | 5 | No | Yes | 1 | OFF | OFF | (0) No event | 15 | No | Yes | 1 | OFF | OFF
3812 | No | Idem case 3810 but in 1P+N network mode | Manual | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | OFF | OFF | (1) Turn off Source 1 | 5 | No | Yes | 1 | OFF | OFF | (0) No event | 15 | No | Yes | 1 | OFF | OFF
3820 | No | Product in manual mode, product in P1 with both S1 and S2 available, change prio to S2 but product stays in P1 | Manual | 3P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | OFF | OFF | (10) Toggle priority source | 5 | Yes | Yes | 1 | OFF | OFF | (0) No event | 15 | Yes | Yes | 1 | OFF | OFF
3822 | No | Idem case 3820 but in 1P+N network mode | Manual | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | OFF | OFF | (10) Toggle priority source | 5 | Yes | Yes | 1 | OFF | OFF | (0) No event | 15 | Yes | Yes | 1 | OFF | OFF
3830 | No | Product in manual mode, product in P2 with only S2 available, then S1 returns but product stays in P2 | Manual | 3P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | No | Yes | 2 | OFF | OFF | (3) Turn on Source 1 | 5 | Yes | Yes | 2 | OFF | OFF | (0) No event | 15 | Yes | Yes | 2 | OFF | OFF
3832 | No | Idem case 3830 but in 1P+N network mode | Manual | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | No | Yes | 2 | OFF | OFF | (3) Turn on Source 1 | 5 | Yes | Yes | 2 | OFF | OFF | (0) No event | 15 | Yes | Yes | 2 | OFF | OFF
3840 | No | Product in manual mode, product in P2 with both S1 and S2 available, prio on S2, then change prio to S1 but product stays in P2 | Manual | 3P+N | M/M | (O) Priority enabled | (C) Prio Source 2 | (O) Auto | No | 0 | 0 | Yes | Yes | 2 | OFF | OFF | (10) Toggle priority source | 5 | Yes | Yes | 2 | OFF | OFF | (0) No event | 15 | Yes | Yes | 2 | OFF | OFF
3842 | No | Idem case 3840 but in 1P+N network mode | Manual | 1P+N | M/M | (O) Priority enabled | (C) Prio Source 2 | (O) Auto | No | 0 | 0 | Yes | Yes | 2 | OFF | OFF | (10) Toggle priority source | 5 | Yes | Yes | 2 | OFF | OFF | (0) No event | 15 | Yes | Yes | 2 | OFF | OFF

## ATYS_g_M_mono
|  |  | Config | [8 empty] | Initial state |  |  |  |  | Event1 |  | State1 |  |  |  |  | Event2 |  | State2 |  |  |  |  | Event3 |  | State3
Test case | Enable ? | Comments or test case description | Mode | Network | Network Application | InputFct1 | InputFct2 | InputFct3 | Stop in 0 ? | RT (s) | FT (s) | S1 available ? | S2 available ? | Position | GenSet | Product Availability | Description | Post-event timer (s) | S1 available ? | S2 available ? | Position | GenSet | Product Availability | Description | Post-event timer (s) | S1 available ? | S2 available ? | Position | GenSet | Product Availability | Description | Post-event timer (s) | S1 available ? | S2 available ? | Position | GenSet | Product Availability
12 | Yes | Basic in M/G: loss of S1, check that StartGen becomes ON and then that the product goes to P2 | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | No | 1 | No check | ON | (1) Turn off Source 1 | 6 | No | No | 1 | ON | OFF | (4) Turn on Source 2 | 6 | No | Yes | 2 | ON | ON
22 | Yes | Test come back in P1 when S1 returns | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (3) Turn on Source 1 | 8 | Yes | Yes | 1 | ON | ON
32 | Yes | Loss of S1, StartGen ON but S1 comes back : check StartGen shuts immediatly OFF and product is still in P1 | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | No | 1 | No check | ON | (1) Turn off Source 1 | 6 | No | No | 1 | ON | OFF | (3) Turn on Source 1 | 8 | Yes | No | 1 | OFF | ON
82 | Yes | Product in P2 with only S2 available, manual retransfert mode, then S1 comes back but check that product stays in P2 | Auto | 1P+N | M/G | (C) Manual retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (3) Turn on Source 1 | 8 | Yes | Yes | 2 | ON | ON | (1) Turn off Source 1 | 3 | No | Yes | 2 | ON | ON
112 | Yes | Loss of S1 but no start of the Gen S2 : check product stays in P1 and no more available | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | No | 1 | No check | ON | (1) Turn off Source 1 | 6 | No | No | 1 | ON | OFF
182 | Yes | Product in P2 with only S2 available, loss of S2 : check that product still in P2 but no more available | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (2) Turn off Source 2 | 6 | No | No | 2 | ON | OFF
192 | Yes | Idem case 180 but then S2 comes back : check product is available again in P2 | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (2) Turn off Source 2 | 6 | No | No | 2 | ON | OFF | (4) Turn on Source 2 | 8 | No | Yes | 2 | ON | ON
202 | Yes | Idem case 180 but then S1 comes back : check product is available again but in P1 and StartGen OFF | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (2) Turn off Source 2 | 6 | No | No | 2 | ON | OFF | (3) Turn on Source 1 | 8 | Yes | No | 1 | OFF | ON
212 | Yes | Both S1 and S2 available, product in P1, loss of S2 : check StartGen is still OFF, product vailable in P1 | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | No check | ON | (2) Turn off Source 2 | 6 | Yes | No | 1 | OFF | ON
242 | Yes | Product in P2 with only S2 available, then inhibit auto mode : check that product is no more available, and then return to initial state | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (8) Toggle state of inhibit auto option | 6 | No | Yes | 2 | ON | OFF | (8) Toggle state of inhibit auto option | 6 | No | Yes | 2 | ON | ON
252 | Yes | Product in P2 with only S2 available, then inhibit auto mode and S1 comes back : check that product stays in P2 | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (8) Toggle state of inhibit auto option | 6 | No | Yes | 2 | ON | OFF | (3) Turn on Source 1 | 8 | Yes | Yes | 2 | ON | OFF
262 | Yes | Idem case 252 but then enable again auto mode and check that the products switches to P1 | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (8) Toggle state of inhibit auto option | 6 | No | Yes | 2 | ON | OFF | (3) Turn on Source 1 | 8 | Yes | Yes | 2 | ON | OFF | (8) Toggle state of inhibit auto option | 245 | Yes | Yes | 1 | OFF | ON
382 | Yes | Test on load : starts in P1, check that StartGen becomes ON, go to P2 | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | No | 1 | No check | ON | (11) Toggle state of on load test option | 10 | Yes | No | 1 | ON | ON | (4) Turn on Source 2 | 10 | Yes | Yes | 2 | ON | ON
442 | Yes | Idem case 382 but then inhibit auto mode and disable test on load : check that the product stays in P2 | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | No check | ON | (11) Toggle state of on load test option | 15 | Yes | Yes | 2 | ON | ON | (8) Toggle state of inhibit auto option | 6 | Yes | Yes | 2 | ON | OFF | (11) Toggle state of on load test option | 5 | Yes | Yes | 2 | ON | OFF
472 | Yes | Test on load and then disable it : check product comes back in P1 | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | No check | ON | (11) Toggle state of on load test option | 15 | Yes | Yes | 2 | ON | ON | (11) Toggle state of on load test option | 10 | Yes | Yes | 1 | ON | ON
482 | Yes | Inhibit auto mode and then start test on load : check that product stays in S1 | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | No | 1 | No check | ON | (8) Toggle state of inhibit auto option | 6 | Yes | No | 1 | No check | OFF | (11) Toggle state of on load test option | 6 | Yes | No | 1 | No check | OFF
522 | Yes | Loss of S1 with manual retransfert mode enabled, turn on S2 and check that the product goes to P2 | Auto | 1P+N | M/G | (C) Manual retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | No | 1 | No check | ON | (1) Turn off Source 1 | 6 | No | No | 1 | ON | OFF | (4) Turn on Source 2 | 8 | No | Yes | 2 | ON | ON
552 | Yes | Product is in P2 with both S1 and S2 available, with manual retransfert mode enabled, then disabled this mode and check that product comes back to P1 | Auto | 1P+N | M/G | (C) Manual retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (3) Turn on Source 1 | 8 | Yes | Yes | 2 | ON | ON | (7) Toggle state of retransfer option | 245 | Yes | Yes | 1 | OFF | ON
602 | Yes | Product in P2, S1 comes back, check that product comes back to P1 and then wait to test cooldown timer (240 s after main returns, StartGen must stop) | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 1 | ON | ON | (0) No event | 245 | Yes | Yes | 1 | OFF | ON
812 | Yes | Product in manual mode, in P1 with only S1 available, then S1 is lost but product doesn't switch to P2 | Manual | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | No | 1 | No check | OFF | (1) Turn off Source 1 | 15 | No | No | 1 | No check | OFF
822 | Yes | Product in manual mode, in P1 with both S1 and S2 available, then S2 is lost | Manual | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | No check | OFF | (2) Turn off Source 2 | 6 | Yes | No | 1 | No check | OFF
1072 | Yes | No source available, product in P1 and manual mode. Then S1 comes back | Manual | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | No | 1 | No check | OFF | (3) Turn on Source 1 | 8 | Yes | No | 1 | No check | OFF
1082 | Yes | No source available, product in P1 and manual mode. Then S2 comes back but product doesn't switch to P2 | Manual | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | No | 1 | No check | OFF | (4) Turn on Source 2 | 8 | No | Yes | 1 | No check | OFF
1112 | Yes | No source available, product in P0 and manual mode. Then S1 comes back but product doesn't switch to P1 | Manual | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | No | 0 | No check | OFF | (3) Turn on Source 1 | 8 | Yes | No | 0 | No check | OFF
1122 | Yes | No source available, product in P0 and manual mode. Then S2 comes back but product doesn't switch to P2 | Manual | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | No | 0 | No check | OFF | (4) Turn on Source 2 | 8 | No | Yes | 0 | No check | OFF
1152 | Yes | No source available, product in P2 and manual mode. Then S1 comes back but product doesn't switch to P1 | Manual | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | No | 2 | No check | OFF | (3) Turn on Source 1 | 8 | Yes | No | 2 | No check | OFF
1162 | Yes | No source available, product in P2 and manual mode. Then S2 comes back | Manual | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | No | 2 | No check | OFF | (4) Turn on Source 2 | 8 | No | Yes | 2 | No check | OFF
1172 | Yes | Loss of S1, check that StartGen becomes ON but then open front control panel : the product doesn't switch to P2 | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | No | 1 | No check | ON | (1) Turn off Source 1 | 6 | No | No | 1 | ON | OFF | (12) Manually open front control panel | 5 | No | Yes | 1 | ON | OFF | (4) Turn on Source 2 | 8 | No | Yes | 1 | ON | OFF
2100 | No | Reference test for fail timer in M/G mode : loss of S1, check that StartGen is ON and that product goes directly to P2 | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | No | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | No | 1 | ON | OFF
2101 | No | Idem case 2100 but with fail timer test to 5s | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 5 | Yes | No | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | No | 1 | OFF | OFF | (0) No event | 5 | No | No | 1 | ON | OFF
2102 | No | Idem case 2100 but with fail timer test to 20s | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 20 | Yes | No | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | No | 1 | OFF | OFF | (0) No event | 25 | No | No | 1 | ON | OFF
2103 | No | Idem case 2100 but with fail timer test to 60s | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 60 | Yes | No | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | No | 1 | OFF | OFF | (0) No event | 65 | No | No | 1 | ON | OFF
2104 | No | Idem case 2103 but S1 state toggles 5 times during fail timer, to check if product ignore this non-significant return of main power supply and goes to P2 anyway | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 60 | Yes | No | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | No | 1 | OFF | OFF | (14) Rapid toggle of Source 1 state 5x | 65 | No | No | 1 | ON | OFF
2105 | No | Idem case 2103 but S1 comes back before end of fail timer, to check if product stays in P1 and StartGen OFF | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 60 | Yes | No | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | No | 1 | OFF | OFF | (3) Turn on Source 1 | 5 | Yes | No | 1 | OFF | ON
2106 | No | Reference test for return timer in M/G mode : product in P2, S1 comes back and check that product comes back to P1 | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | No | Yes | 2 | ON | ON | (3) Turn on Source 1 | 10 | Yes | Yes | 1 | ON | ON
2107 | No | Idem case 2106 but with return timer test to 3 min | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 180 | 0 | No | Yes | 2 | ON | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | ON | ON | (0) No event | 185 | Yes | Yes | 1 | ON | ON
2108 | No | Idem case 2107 but S1 state toggles 5 times during return timer, to check if product ignore non-significant failures of main power supply and switches to P1 anyway | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 180 | 0 | No | Yes | 2 | ON | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | ON | ON | (14) Rapid toggle of Source 1 state 5x | 185 | Yes | Yes | 1 | ON | ON
2109 | No | Idem case 2106 but with return timer test to 10 min | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 600 | 0 | No | Yes | 2 | ON | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | ON | ON | (0) No event | 605 | Yes | Yes | 1 | ON | ON
2110 | No | Idem case 2106 but with return timer test to 30 min | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 600 | 0 | No | Yes | 2 | ON | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | ON | ON | (0) No event | 1805 | Yes | Yes | 1 | ON | ON
2111 | No | Reference test for fail timer in M/M mode: loss of S1 with S2 available, check that the product switches directly to P2 | Auto | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | Yes | 2 | OFF | ON
2112 | No | Idem case 2111 but with fail timer test to 5s | Auto | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 5 | Yes | Yes | 1 | OFF | ON | (1) Turn off Source 1 | 8 | No | Yes | 2 | OFF | ON | (0) No event | 5 | No | Yes | 2 | OFF | ON
2113 | No | Idem case 2111 but with fail timer test to 20s | Auto | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 20 | Yes | Yes | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | Yes | 1 | OFF | ON | (0) No event | 25 | No | Yes | 2 | OFF | ON
2114 | No | Idem case 2111 but with fail timer test to 60s | Auto | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 60 | Yes | Yes | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | Yes | 1 | OFF | ON | (0) No event | 65 | No | Yes | 2 | OFF | ON
2115 | No | Idem case 2113 but S1 state toggles 5 times during fail timer, to check if product ignore this non-significant return of main power supply and goes to P2 anyway | Auto | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 60 | Yes | Yes | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | Yes | 1 | OFF | ON | (14) Rapid toggle of Source 1 state 5x | 65 | No | Yes | 2 | OFF | ON
2116 | No | Idem case 2113 but S1 comes back before end of fail timer, to check if product stays in P1 and StartGen OFF | Auto | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 60 | Yes | Yes | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | Yes | 1 | OFF | ON | (3) Turn on Source 1 | 5 | Yes | Yes | 1 | OFF | ON
2117 | No | Reference test for return timer in M/M mode: product in P2, S1 comes back and check that product comes back to P1 | Auto | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | No | Yes | 2 | OFF | ON | (3) Turn on Source 1 | 10 | Yes | Yes | 1 | OFF | ON | [5 empty] | OFF
2118 | No | Idem case 2117 but with return timer test to 3 min | Auto | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 180 | 0 | No | Yes | 2 | OFF | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | OFF | ON | (0) No event | 185 | Yes | Yes | 1 | OFF | ON
2119 | No | Idem case 2118 but S1 state toggles 5 times during return timer, to check if product ignore non-significant failures of main power supply and switches to P1 anyway | Auto | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 180 | 0 | No | Yes | 2 | OFF | ON | (3) Turn on Source 1 | 6 | Yes | No | 2 | OFF | ON | (14) Rapid toggle of Source 1 state 5x | 185 | Yes | No | 1 | OFF | ON
2020 | No | Idem case 2117 but with return timer test to 10 min | Auto | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 600 | 0 | No | Yes | 2 | OFF | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | OFF | ON | (0) No event | 605 | Yes | Yes | 1 | OFF | ON
2021 | No | Idem case 2117 but with return timer test to 30 min | Auto | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 1800 | 0 | No | Yes | 2 | OFF | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | OFF | ON | (0) No event | 1805 | Yes | Yes | 1 | OFF | ON
3002 | No | Basic in M/M: loss of S1 with S2 available, check that the product goes to P2 | Auto | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | Yes | 2 | OFF | ON
3022 | No | Product in P2 with only S2 available, then loss of S2, S1 comes back | Auto | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | No | Yes | 2 | OFF | ON | (2) Turn off Source 2 | 6 | No | No | 2 | OFF | OFF | (3) Turn on Source 1 | 6 | Yes | No | 1 | OFF | ON
3042 | No | With priority on S2, both S1 and S2 available, loss of S2 : the product must switch to P1 and then S2 comes back : the product must switch again to P2 | Auto | 1P+N | M/M | (O) Priority enabled | (C) Prio Source 2 | (O) Auto | No | 0 | 0 | Yes | Yes | 2 | OFF | ON | (2) Turn off Source 2 | 8 | Yes | No | 1 | OFF | ON | (4) Turn on Source 2 | 10 | Yes | Yes | 2 | OFF | ON
3052 | No | Both S1 and S2 available, priority set to S1, then toggle priority to S2 : the product must switch to P2 | Auto | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | OFF | ON | (10) Toggle priority source | 10 | Yes | Yes | 2 | OFF | ON
3062 | No | Product in P2, S2 only available. Change priority to S1, and then S1 comes back but product must stays in P2 | Auto | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | No | Yes | 2 | OFF | ON | (9) Toggle state of priority enable option | 6 | No | Yes | 2 | OFF | ON | (3) Turn on Source 1 | 10 | Yes | Yes | 2 | OFF | ON
3072 | No | Set priority to S2 but disable priority with input 1. Product is in P1, S2 comes back but produt stays in P1 | Auto | 1P+N | M/M | (C) Priority disabled | (C) Prio Source 2 | (O) Auto | No | 0 | 0 | Yes | No | 1 | OFF | ON | (4) Turn on Source 2 | 6 | Yes | Yes | 1 | OFF | ON
3082 | No | Set priority to S1 but disable priority with input 1. Product is in P2, S1 comes back but produt stays in P2 | Auto | 1P+N | M/M | (C) Priority disabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | No | Yes | 2 | OFF | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | OFF | ON
3092 | No | Product in P2, S2 only available. Inhibit auto mode, then S1 comes back, S2 is lost but product stays in P2 | Auto | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | No | Yes | 2 | OFF | ON | (8) Toggle state of inhibit auto option | 6 | No | Yes | 2 | OFF | OFF | (3) Turn on Source 1 | 3 | Yes | Yes | 2 | OFF | OFF | (2) Turn off Source 2 | 3 | Yes | No | 2 | OFF | OFF
3102 | No | Product in P1, S1 only available and priority is set to S2. Inhibit auto mode, then S2 comes back, S1 is lost but product stays in P1 | Auto | 1P+N | M/M | (O) Priority enabled | (C) Prio Source 2 | (O) Auto | No | 0 | 0 | Yes | No | 1 | OFF | ON | (8) Toggle state of inhibit auto option | 6 | Yes | No | 1 | OFF | OFF | (4) Turn on Source 2 | 3 | Yes | Yes | 1 | OFF | OFF | (1) Turn off Source 1 | 3 | No | Yes | 1 | OFF | OFF
3812 | No | Product in manual mode, product in P1 with both S1 and S2 available, loss of S1 but product stays in P1 | Manual | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | OFF | OFF | (1) Turn off Source 1 | 5 | No | Yes | 1 | OFF | OFF | (0) No event | 15 | No | Yes | 1 | OFF | OFF
3822 | No | Product in manual mode, product in P1 with both S1 and S2 available, change prio to S2 but product stays in P1 | Manual | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | OFF | OFF | (10) Toggle priority source | 5 | Yes | Yes | 1 | OFF | OFF | (0) No event | 15 | Yes | Yes | 1 | OFF | OFF
3832 | No | Product in manual mode, product in P2 with only S2 available, then S1 returns but product stays in P2 | Manual | 1P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | No | Yes | 2 | OFF | OFF | (3) Turn on Source 1 | 5 | Yes | Yes | 2 | OFF | OFF | (0) No event | 15 | Yes | Yes | 2 | OFF | OFF
3842 | No | Product in manual mode, product in P2 with both S1 and S2 available, prio on S2, then change prio to S1 but product stays in P2 | Manual | 1P+N | M/M | (O) Priority enabled | (C) Prio Source 2 | (O) Auto | No | 0 | 0 | Yes | Yes | 2 | OFF | OFF | (10) Toggle priority source | 5 | Yes | Yes | 2 | OFF | OFF | (0) No event | 15 | Yes | Yes | 2 | OFF | OFF

## ATYS_t_M
|  |  | Config | [8 empty] | Initial state |  |  |  |  | Event1 |  | State1 |  |  |  |  | Event2 |  | State2 |  |  |  |  | Event3 |  | State3
Test case | Enable ? | Comments or test case description | Mode | Network | Priority Enabled ? | InputFct1 | InputFct2 | InputFct3 | Stop in 0 ? | RT (s) | FT (s) | S1 available ? | S2 available ? | Position | GenSet | Product Availability | Description | Post-event timer (s) | S1 available ? | S2 available ? | Position | GenSet | Product Availability | Description | Post-event timer (s) | S1 available ? | S2 available ? | Position | GenSet | Product Availability | Description | Post-event timer (s) | S1 available ? | S2 available ? | Position | GenSet | Product Availability
2300 | No | Reference test for fail and return timer : loss of S1, go to P2, then S1 comes back and the product switches again to P1 | Auto | 3P+N | Yes | (O) Go to 0 disabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | No check | ON | (1) Turn off Source 1 | 4 | No | Yes | 2 | No check | ON | (3) Turn on Source 1 | 8 | Yes | Yes | 1 | No check | ON
2301 | No | Idem case 2300 but with fail timer test to 3s and return timer to 3 min | Auto | 3P+N | Yes | (O) Go to 0 disabled | (O) Prio Source 1 | (O) Auto | No | 180 | 3 | Yes | Yes | 1 | No check | ON | (1) Turn off Source 1 | 4 | No | Yes | 2 | No check | ON | (3) Turn on Source 1 | 185 | Yes | Yes | 1 | No check | ON
2302 | No | Idem case 2300 but with fail timer test to 10s and return timer to 10 min | Auto | 3P+N | Yes | (O) Go to 0 disabled | (O) Prio Source 1 | (O) Auto | No | 600 | 10 | Yes | Yes | 1 | No check | ON | (1) Turn off Source 1 | 11 | No | Yes | 2 | No check | ON | (3) Turn on Source 1 | 605 | Yes | Yes | 1 | No check | ON
2303 | No | Idem case 2300 but with fail timer test to 30s and return timer to 30 min | Auto | 3P+N | Yes | (O) Go to 0 disabled | (O) Prio Source 1 | (O) Auto | No | 1800 | 30 | Yes | Yes | 1 | No check | ON | (1) Turn off Source 1 | 31 | No | Yes | 2 | No check | ON | (3) Turn on Source 1 | 1805 | Yes | Yes | 1 | No check | ON
3000 | No | Basic in M/M: loss of S1 with S2 available, check that the product goes to P2 | Auto | 3P+N | Yes | (O) Go to 0 disabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | No check | ON | (1) Turn off Source 1 | 8 | No | Yes | 2 | No check | ON
3001 | No | Idem case 3000 but not all 3 phases of S1 are lost, only one | Auto | 3P+N | Yes | (O) Go to 0 disabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | No check | ON | (5) Lose one phase of Source 1 | 6 | Yes | Yes | 2 | No check | ON
3020 | No | Product in P2 with only S2 available, then loss of S2, S1 comes back | Auto | 3P+N | Yes | (O) Go to 0 disabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | No | Yes | 2 | No check | ON | (2) Turn off Source 2 | 6 | No | No | 2 | No check | OFF | (3) Turn on Source 1 | 6 | Yes | No | 1 | No check | ON
3040 | No | With priority on S2, both S1 and S2 available, loss of S2 : the product must switch to P1 and then S2 comes back : the product must switch again to P2 | Auto | 3P+N | Yes | (O) Go to 0 disabled | (C) Prio Source 2 | (O) Auto | No | 0 | 0 | Yes | Yes | 2 | No check | ON | (2) Turn off Source 2 | 8 | Yes | No | 1 | No check | ON | (4) Turn on Source 2 | 10 | Yes | Yes | 2 | No check | ON
3041 | No | Idem case 3040 but not all 3 phases of S2 are lost, only one | Auto | 3P+N | Yes | (O) Go to 0 disabled | (C) Prio Source 2 | (O) Auto | No | 0 | 0 | Yes | Yes | 2 | No check | ON | (6) Lose one phase of Source 2 | 8 | Yes | Yes | 1 | No check | ON
3050 | No | Both S1 and S2 available, priority set to S1, then toggle priority to S2 : the product must switch to P2 | Auto | 3P+N | Yes | (O) Go to 0 disabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | No check | ON | (10) Toggle priority source | 10 | Yes | Yes | 2 | No check | ON
3073 | No | Set priority to S2 but disable priority with DIP switch. Product is in P1, S2 comes back but produt stays in P1 | Auto | 3P+N | No | (O) Go to 0 disabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | Yes | No | 1 | No check | ON | (4) Turn on Source 2 | 6 | Yes | Yes | 1 | No check | ON
3083 | No | Set priority to S1 but disable priority with DIP switch. Product is in P2, S1 comes back but produt stays in P2 | Auto | 3P+N | No | (O) Go to 0 disabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | No | Yes | 2 | No check | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | No check | ON
3090 | No | Product in P2, S2 only available. Inhibit auto mode, then S1 comes back, S2 is lost but product stays in P2 | Auto | 3P+N | Yes | (O) Go to 0 disabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | No | Yes | 2 | No check | ON | (8) Toggle state of inhibit auto option | 6 | No | Yes | 2 | No check | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | No check | ON | (2) Turn off Source 2 | 3 | Yes | No | 2 | No check | ON
3101 | No | Product in P1, S1 only available and priority is set to S2. Inhibit auto mode, then S2 comes back, S1 is lost but product stays in P1 | Auto | 3P+N | Yes | (O) Go to 0 disabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | Yes | No | 1 | No check | ON | (8) Toggle state of inhibit auto option | 6 | Yes | No | 1 | No check | ON | (4) Turn on Source 2 | 6 | Yes | Yes | 1 | No check | ON | (2) Turn off Source 2 | 3 | No | Yes | 1 | No check | ON
3200 | No | Product in P1 with both S1 and S2 available, then send go to P0 cmd, check i product switches to 0, then disable cmd but product stays in P0. At the end, enable and disable inhibit auto option to reset default in product and return to P1 | Auto | 3P+N | Yes | (O) Go to 0 disabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | No check | ON | (15) Toggle state of go to position 0 option | 6 | Yes | Yes | 0 | No check | ON | (15) Toggle state of go to position 0 option | 6 | Yes | Yes | 0 | No check | ON | (16) Double toggle of inhibit auto option | 6 | Yes | Yes | 1 | No check | ON
3201 | No | Idem case 3200 but starting in P2, only S2 is available | Auto | 3P+N | Yes | (O) Go to 0 disabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | No | Yes | 2 | No check | ON | (15) Toggle state of go to position 0 option | 6 | No | Yes | 2 | No check | ON | (15) Toggle state of go to position 0 option | 6 | No | Yes | 2 | No check | ON | (16) Double toggle of inhibit auto option | 6 | No | Yes | 2 | No check | ON
3202 | No | Idem case 3200 but starting in P2, priority is set to S2 | Auto | 3P+N | Yes | (O) Go to 0 disabled | (C) Prio Source 2 | (O) Auto | No | 0 | 0 | Yes | Yes | 2 | No check | ON | (15) Toggle state of go to position 0 option | 6 | Yes | Yes | 0 | No check | ON | (15) Toggle state of go to position 0 option | 6 | Yes | Yes | 0 | No check | ON | (16) Double toggle of inhibit auto option | 6 | Yes | Yes | 2 | No check | ON
3203 | No | Idem case 3200 but only S1 is available | Auto | 3P+N | Yes | (O) Go to 0 disabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | Yes | No | 1 | No check | ON | (15) Toggle state of go to position 0 option | 6 | Yes | No | 1 | No check | ON | (15) Toggle state of go to position 0 option | 6 | Yes | No | 1 | No check | ON | (16) Double toggle of inhibit auto option | 6 | Yes | No | 1 | No check | ON
3204 | No | Idem case 3200 but with inhibit auto mode | Auto | 3P+N | Yes | (O) Go to 0 disabled | (O) Prio Source 1 | (C) Inhibit Auto | No | 0 | 0 | Yes | Yes | 1 | No check | ON | (15) Toggle state of go to position 0 option | 6 | Yes | Yes | 0 | No check | ON | (15) Toggle state of go to position 0 option | 6 | Yes | Yes | 0 | No check | ON
3810 | Yes | Product in manual mode, product in P1 with both S1 and S2 available, loss of S1 but product stays in P1 | Manual | 3P+N | M/M | (O) Go to 0 disabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | No check | ON | (1) Turn off Source 1 | 5 | No | Yes | 1 | No check | ON | (0) No event | 15 | No | Yes | 1 | No check | ON
3820 | Yes | Product in manual mode, product in P1 with both S1 and S2 available, change prio to S2 but product stays in P1 | Manual | 3P+N | M/M | (O) Go to 0 disabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | No check | ON | (10) Toggle priority source | 5 | Yes | Yes | 1 | No check | ON | (0) No event | 15 | Yes | Yes | 1 | No check | ON
3830 | Yes | Product in manual mode, product in P2 with only S2 available, then S1 returns but product stays in P2 | Manual | 3P+N | M/M | (O) Go to 0 disabled | (O) Prio Source 1 | (O) Auto | No | 0 | 0 | No | Yes | 2 | No check | ON | (3) Turn on Source 1 | 5 | Yes | Yes | 2 | No check | ON | (0) No event | 15 | Yes | Yes | 2 | No check | ON
3840 | Yes | Product in manual mode, product in P2 with both S1 and S2 available, prio on S2, then change prio to S1 but product stays in P2 | Manual | 3P+N | M/M | (O) Go to 0 disabled | (C) Prio Source 2 | (O) Auto | No | 0 | 0 | Yes | Yes | 2 | No check | ON | (10) Toggle priority source | 5 | Yes | Yes | 2 | No check | ON | (0) No event | 15 | Yes | Yes | 2 | No check | ON

## ATYS_a_M
|  |  | Config | [8 empty] | Initial state |  |  |  |  | Event1 |  | State1 |  |  |  |  | Event2 |  | State2 |  |  |  |  | Event3 |  | State3
Test case | Enable ? | Comments or test case description | Mode | Network | Network Application | InputFct1 | InputFct2 | InputFct3 | Stop in 0 ? | RT (s) | FT (s) | S1 available ? | S2 available ? | Position | GenSet | Product Availability | Description | Post-event timer (s) | S1 available ? | S2 available ? | Position | GenSet | Product Availability | Description | Post-event timer (s) | S1 available ? | S2 available ? | Position | GenSet | Product Availability | Description | Post-event timer (s) | S1 available ? | S2 available ? | Position | GenSet | Product Availability
2011 | Yes | Reference test for fail timer in M/M mode: loss of S1 with S2 available, check that the product switches directly to P2 after 2s | Auto | 3P+N | M/M | (O) Go to 0 disabled | (O) Default | (O) Auto | No | 2 | 2 | Yes | No | 1 | No check | ON | (1) Turn off Source 1 | 6 | No | No | 1 | No check | OFF
2017 | Yes | Reference test for return timer in M/M mode: product in P2, S1 comes back and check that product comes back to P1 within 2s | Auto | 3P+N | M/M | (O) Go to 0 disabled | (O) Default | (O) Auto | No | 2 | 2 | No | Yes | 2 | No check | ON | (3) Turn on Source 1 | 4 | Yes | Yes | 1 | No check | ON
3000 | Yes | Basic in M/M: loss of S1 with S2 available, check that the product goes to P2 | Auto | 3P+N | M/M | (O) Go to 0 disabled | (O) Default | (O) Auto | No | 2 | 2 | Yes | Yes | 1 | No check | ON | (1) Turn off Source 1 | 8 | No | Yes | 2 | No check | ON
3001 | Yes | Idem case 3000 but not all 3 phases of S1 are lost, only one | Auto | 3P+N | M/M | (O) Go to 0 disabled | (O) Default | (O) Auto | No | 2 | 2 | Yes | Yes | 1 | No check | ON | (5) Lose one phase of Source 1 | 6 | Yes | Yes | 1 | No check | ON
3020 | Yes | Product in P2 with only S2 available, then loss of S2, S1 comes back | Auto | 3P+N | M/M | (O) Go to 0 disabled | (O) Default | (O) Auto | No | 2 | 2 | No | Yes | 2 | No check | ON | (2) Turn off Source 2 | 6 | No | No | 2 | No check | OFF | (3) Turn on Source 1 | 6 | Yes | No | 1 | No check | ON
3090 | Yes | Product in P2, S2 only available. Inhibit auto mode, then S1 comes back, S2 is lost but product stays in P2 | Auto | 3P+N | M/M | (O) Go to 0 disabled | (O) Default | (O) Auto | No | 2 | 2 | No | Yes | 2 | No check | ON | (8) Toggle state of inhibit auto option | 6 | No | Yes | 2 | No check | ON | (3) Turn on Source 1 | 3 | Yes | Yes | 2 | No check | ON | (2) Turn off Source 2 | 3 | Yes | No | 2 | No check | ON
3201 | Yes | Idem case 3200 but starting in P2, only S2 is available | Auto | 3P+N | M/M | (O) Go to 0 disabled | (O) Default | (O) Auto | No | 2 | 2 | No | Yes | 2 | No check | ON | (15) Toggle state of go to position 0 option | 6 | No | Yes | 2 | No check | ON | (15) Toggle state of go to position 0 option | 6 | No | Yes | 2 | No check | ON | (16) Double toggle of inhibit auto option | 6 | No | Yes | 2 | No check | ON
3203 | Yes | Idem case 3200 but only S1 is available | Auto | 3P+N | M/M | (O) Go to 0 disabled | (O) Default | (O) Auto | No | 2 | 2 | Yes | No | 1 | No check | ON | (15) Toggle state of go to position 0 option | 6 | Yes | No | 1 | No check | ON | (15) Toggle state of go to position 0 option | 6 | Yes | No | 1 | No check | ON | (16) Double toggle of inhibit auto option | 6 | Yes | No | 1 | No check | ON
3204 | Yes | Idem case 3200 but with inhibit auto mode | Auto | 3P+N | M/M | (O) Go to 0 disabled | (O) Default | (C) Inhibit Auto | No | 2 | 2 | Yes | Yes | 1 | No check | ON | (15) Toggle state of go to position 0 option | 6 | Yes | Yes | 0 | No check | ON | (15) Toggle state of go to position 0 option | 6 | Yes | Yes | 0 | No check | ON
3810 | No | Product in manual mode, product in P1 with both S1 and S2 available, loss of S1 but product stays in P1 | Manual | 3P+N | M/M | (O) Priority enabled | (O) Default | (O) Auto | No | 0 | 0 | Yes | Yes | 1 | No check | ON | (1) Turn off Source 1 | 5 | No | Yes | 1 | No check | ON | (0) No event | 15 | No | Yes | 1 | No check | ON
3830 | No | Product in manual mode, product in P2 with only S2 available, then S1 returns but product stays in P2 | Manual | 3P+N | M/M | (O) Priority enabled | (O) Default | (O) Auto | No | 0 | 0 | No | Yes | 2 | No check | ON | (3) Turn on Source 1 | 5 | Yes | Yes | 2 | No check | ON | (0) No event | 15 | Yes | Yes | 2 | No check | ON

## ATYS_g_M_SDMO_tri
|  |  | Config | [8 empty] | Initial state |  |  |  |  | Event1 |  | State1 |  |  |  |  | Event2 |  | State2 |  |  |  |  | Event3 |  | State3
Test case | Enable ? | Comments or test case description | Mode | Network | EJP mode | InputFct1 | InputFct2 | InputFct3 | Stop in 0 ? | RT (s) | FT (s) | S1 available ? | S2 available ? | Position | GenSet | Report EJP | Description | Post-event timer (s) | S1 available ? | S2 available ? | Position | GenSet | Report EJP | Description | Post-event timer (s) | S1 available ? | S2 available ? | Position | GenSet | Report EJP | Description | Post-event timer (s) | S1 available ? | S2 available ? | Position | GenSet | Report EJP
4000 | Yes | Basic in M/G: loss of S1, check that StartGen becomes ON and then that the product goes to P2 | Auto | 3P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | Yes | No | 1 | No check | OFF | (1) Turn off Source 1 | 6 | No | No | 1 | ON | OFF | (4) Turn on Source 2 | 5 | No | Yes | 2 | ON | OFF
4001 | Yes | Test come back in P1 when S1 returns | Auto | 3P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | No | Yes | 2 | ON | OFF | (3) Turn on Source 1 | 6 | Yes | Yes | 1 | ON | OFF | (0) No event | 125 | Yes | Yes | 1 | ON | OFF
4002 | Yes | Product is in P1, and recieve preavis EJP. Wait 20 min until StartGen becomes ON and switches to P2 | Auto | 3P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | Yes | No | 1 | No check | OFF | (17) Toggle preavis EJP input state | 5 | Yes | No | 1 | OFF | OFF | (0) No event | 1205 | Yes | No | 1 | ON | ON | (4) Turn on Source 2 | 8 | Yes | Yes | 2 | ON | ON
4003 | Yes | Product is in P2 because EJP is already active, preavis EJP ends : wait 10 min until product switches again to P1 and StartGen becomes OFF | Auto | 3P+N | UTIL | (O) Auto retransfer | (C) Preavis EJP ON | (O) Top EJP OFF | No | 0 | 0 | Yes | Yes | 2 | ON | ON | (17) Toggle preavis EJP input state | 605 | Yes | Yes | 1 | ON | OFF | (0) No event | 120 | Yes | Yes | 1 | OFF | OFF
4004 | Yes | Product is in P1, and recieve top EJP, check that StartGen becomes directly ON and product switches to P2 | Auto | 3P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | Yes | No | 1 | No check | OFF | (18) Toggle top EJP input state | 5 | Yes | No | 1 | ON | ON | (4) Turn on Source 2 | 8 | Yes | Yes | 2 | ON | ON
4005 | Yes | Product is in P2 because EJP is already active, top EJP ends : wait 10 min until product switches again to P1 and StartGen becomes OFF | Auto | 3P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (C) Top EJP ON | No | 0 | 0 | Yes | Yes | 2 | ON | ON | (18) Toggle top EJP input state | 605 | Yes | Yes | 1 | ON | OFF | (0) No event | 120 | Yes | Yes | 1 | OFF | OFF
4006 | Yes | Test return in P1 when S1 comes back and cooldown timer to stop StartGen | Auto | 3P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | No | Yes | 2 | ON | OFF | (3) Turn on Source 1 | 6 | Yes | Yes | 1 | ON | OFF | (0) No event | 125 | Yes | Yes | 1 | OFF | OFF
4007 | Yes | Idem case 4006 but auto retransfer is disabled, so the product stays in P2 after S1 return | Auto | 3P+N | UTIL | (C) Manual retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | No | Yes | 2 | ON | OFF | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | ON | OFF
4008 | Yes | Product is in P2 because EJP is already active, top EJP ends but auto retransfer is disabled : wait 10 min to check if product stays in P2 | auto | 3P+N | UTIL | (C) Manual retransfer | (O) Preavis EJP OFF | (C) Top EJP ON | No | 0 | 0 | Yes | Yes | 2 | ON | ON | (18) Toggle top EJP input state | 605 | Yes | Yes | 2 | ON | OFF
4009 | Yes | Product is in P2 because EJP is already active with both S1 and S2 available, then S2 is lost so product must switch to P1 | Auto | 3P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (C) Top EJP ON | No | 0 | 0 | Yes | Yes | 2 | ON | ON | (2) Turn off Source 2 | 8 | Yes | No | 1 | ON | ON
4010 | Yes | Test fail timer : loss of S1, check that StartGen becomes ON after 20s | Auto | 3P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 20 | Yes | No | 1 | OFF | OFF | (1) Turn off Source 1 | 25 | No | No | 1 | ON | OFF
4011 | Yes | Test return timer: product is in P2 because S1 is not available, then S1 comes back so wait 10 min until product switches again to P1 | Auto | 3P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 600 | 0 | No | Yes | 2 | ON | OFF | (3) Turn on Source 1 | 605 | Yes | Yes | 1 | ON | OFF
4500 | No | Idem case 4000 but in 1P+N network mode | Auto | 1P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | Yes | No | 1 | No check | OFF | (1) Turn off Source 1 | 6 | No | No | 1 | ON | OFF | (4) Turn on Source 2 | 5 | No | Yes | 2 | ON | OFF
4501 | No | Idem case 4001 but in 1P+N network mode | Auto | 1P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | No | Yes | 2 | ON | OFF | (3) Turn on Source 1 | 6 | Yes | Yes | 1 | ON | OFF | (0) No event | 125 | Yes | Yes | 1 | ON | OFF
4502 | No | Idem case 4002 but in 1P+N network mode | Auto | 1P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | Yes | No | 1 | No check | OFF | (17) Toggle preavis EJP input state | 5 | Yes | No | 1 | OFF | OFF | (0) No event | 1205 | Yes | No | 1 | ON | ON | (4) Turn on Source 2 | 8 | Yes | Yes | 2 | ON | ON
4503 | No | Idem case 4003 but in 1P+N network mode | Auto | 1P+N | UTIL | (O) Auto retransfer | (C) Preavis EJP ON | (O) Top EJP OFF | No | 0 | 0 | Yes | Yes | 2 | ON | ON | (17) Toggle preavis EJP input state | 605 | Yes | Yes | 1 | ON | OFF | (0) No event | 120 | Yes | Yes | 1 | OFF | OFF
4504 | No | Idem case 4004 but in 1P+N network mode | Auto | 1P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | Yes | No | 1 | No check | OFF | (18) Toggle top EJP input state | 5 | Yes | No | 1 | ON | ON | (4) Turn on Source 2 | 8 | Yes | Yes | 2 | ON | ON
4505 | No | Idem case 4005 but in 1P+N network mode | Auto | 1P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (C) Top EJP ON | No | 0 | 0 | Yes | Yes | 2 | ON | ON | (18) Toggle top EJP input state | 605 | Yes | Yes | 1 | ON | OFF | (0) No event | 120 | Yes | Yes | 1 | OFF | OFF
4506 | No | Idem case 4006 but in 1P+N network mode | Auto | 1P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | No | Yes | 2 | ON | OFF | (3) Turn on Source 1 | 6 | Yes | Yes | 1 | ON | OFF | (0) No event | 125 | Yes | Yes | 1 | OFF | OFF
4507 | No | Idem case 4007 but in 1P+N network mode | Auto | 1P+N | UTIL | (C) Manual retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | No | Yes | 2 | ON | OFF | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | ON | OFF
4508 | No | Idem case 4008 but in 1P+N network mode | Auto | 1P+N | UTIL | (C) Manual retransfer | (O) Preavis EJP OFF | (C) Top EJP ON | No | 0 | 0 | Yes | Yes | 2 | ON | ON | (18) Toggle top EJP input state | 605 | Yes | Yes | 2 | ON | OFF
4509 | No | Idem case 4009 but in 1P+N network mode | Auto | 1P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (C) Top EJP ON | No | 0 | 0 | Yes | Yes | 2 | ON | ON | (2) Turn off Source 2 | 8 | Yes | No | 1 | ON | ON
4510 | No | Idem case 4010 but in 1P+N network mode | Auto | 1P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 20 | Yes | No | 1 | OFF | OFF | (1) Turn off Source 1 | 25 | No | No | 1 | ON | OFF
4511 | No | Idem case 4011 but in 1P+N network mode | Auto | 1P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 600 | 0 | No | Yes | 2 | ON | OFF | (3) Turn on Source 1 | 605 | Yes | Yes | 1 | ON | OFF
4810 | No | Product in manual mode, in P1 with only S1 available, then S1 is lost but product doesn't switch to P2 | Manual | 3P+N | M/G | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | Yes | No | 1 | No check | OFF | (1) Turn off Source 1 | 15 | No | No | 1 | No check | OFF
4812 | No | Idem case 4810 but in 1P+N network mode | Manual | 1P+N | M/G | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | Yes | No | 1 | No check | OFF | (1) Turn off Source 1 | 15 | No | No | 1 | No check | OFF
4820 | No | Product in manual mode, in P1 with both S1 and S2 available, then S2 is lost | Manual | 3P+N | M/G | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | Yes | Yes | 1 | No check | OFF | (2) Turn off Source 2 | 6 | Yes | No | 1 | No check | OFF
4822 | No | Idem case 4820 but in 1P+N network mode | Manual | 1P+N | M/G | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | Yes | Yes | 1 | No check | OFF | (2) Turn off Source 2 | 6 | Yes | No | 1 | No check | OFF
4830 | No | No source available, product in P1 and manual mode. Then S1 comes back | Manual | 3P+N | M/G | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | No | No | 1 | No check | OFF | (3) Turn on Source 1 | 8 | Yes | No | 1 | No check | OFF
4832 | No | Idem case 4830 but in 1P+N network mode | Manual | 1P+N | M/G | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | No | No | 1 | No check | OFF | (3) Turn on Source 1 | 8 | Yes | No | 1 | No check | OFF
4840 | No | No source available, product in P1 and manual mode. Then S2 comes back but product doesn't switch to P2 | Manual | 3P+N | M/G | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | No | No | 1 | No check | OFF | (4) Turn on Source 2 | 8 | No | Yes | 1 | No check | OFF
4842 | No | Idem case 4840 but in 1P+N network mode | Manual | 1P+N | M/G | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | No | No | 1 | No check | OFF | (4) Turn on Source 2 | 8 | No | Yes | 1 | No check | OFF
4850 | No | No source available, product in P0 and manual mode. Then S1 comes back but product doesn't switch to P1 | Manual | 3P+N | M/G | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | No | No | 0 | No check | OFF | (3) Turn on Source 1 | 8 | Yes | No | 0 | No check | OFF
4852 | No | Idem case 4850 but in 1P+N network mode | Manual | 1P+N | M/G | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | No | No | 0 | No check | OFF | (3) Turn on Source 1 | 8 | Yes | No | 0 | No check | OFF
4860 | No | No source available, product in P0 and manual mode. Then S2 comes back but product doesn't switch to P2 | Manual | 3P+N | M/G | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | No | No | 0 | No check | OFF | (4) Turn on Source 2 | 8 | No | Yes | 0 | No check | OFF
4862 | No | Idem case 4860 but in 1P+N network mode | Manual | 1P+N | M/G | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | No | No | 0 | No check | OFF | (4) Turn on Source 2 | 8 | No | Yes | 0 | No check | OFF
4870 | No | No source available, product in P2 and manual mode. Then S1 comes back but product doesn't switch to P1 | Manual | 3P+N | M/G | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | No | No | 2 | No check | OFF | (3) Turn on Source 1 | 8 | Yes | No | 2 | No check | OFF
4872 | No | Idem case 4870 but in 1P+N network mode | Manual | 1P+N | M/G | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | No | No | 2 | No check | OFF | (3) Turn on Source 1 | 8 | Yes | No | 2 | No check | OFF
4880 | No | No source available, product in P2 and manual mode. Then S2 comes back | Manual | 3P+N | M/G | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | No | No | 2 | No check | OFF | (4) Turn on Source 2 | 8 | No | Yes | 2 | No check | OFF
4882 | No | Idem case 4880 but in 1P+N network mode | Manual | 1P+N | M/G | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | No | No | 2 | No check | OFF | (4) Turn on Source 2 | 8 | No | Yes | 2 | No check | OFF
4890 | No | Loss of S1, check that StartGen becomes ON but then open front control panel : the product doesn't switch to P2 | Auto | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | No | 1 | No check | OFF | (1) Turn off Source 1 | 6 | No | No | 1 | ON | OFF | (12) Manually open front control panel | 5 | No | Yes | 1 | ON | OFF | (4) Turn on Source 2 | 8 | No | Yes | 1 | ON | OFF
4892 | No | Idem case 4890 but in 1P+N network mode | Auto | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | No | 1 | No check | OFF | (1) Turn off Source 1 | 6 | No | No | 1 | ON | OFF | (12) Manually open front control panel | 5 | No | Yes | 1 | ON | OFF | (4) Turn on Source 2 | 8 | No | Yes | 1 | ON | OFF
4900 | No | Product in manual mode, send top EJP input but StartGen must stays OFF | Manual | 3P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | No | 1 | OFF | OFF | (18) Toggle top EJP input state | 6 | Yes | No | 1 | OFF | OFF | (4) Turn on Source 2 | 15 | Yes | No | 1 | OFF | OFF
4902 | No | Idem case 4900 but in 1P+N network mode | Manual | 1P+N | M/G | (O) Auto retransfer | (O) Stop test | (O) Auto | No | 0 | 0 | Yes | No | 1 | OFF | OFF | (18) Toggle top EJP input state | 6 | Yes | No | 1 | OFF | OFF | (4) Turn on Source 2 | 15 | Yes | No | 1 | OFF | OFF

## ATYS_g_M_SDMO_mono
|  |  | Config | [8 empty] | Initial state |  |  |  |  | Event1 |  | State1 |  |  |  |  | Event2 |  | State2 |  |  |  |  | Event3 |  | State3
Test case | Enable ? | Comments or test case description | Mode | Network | EJP mode | InputFct1 | InputFct2 | InputFct3 | Stop in 0 ? | RT (s) | FT (s) | S1 available ? | S2 available ? | Position | GenSet | Report EJP | Description | Post-event timer (s) | S1 available ? | S2 available ? | Position | GenSet | Report EJP | Description | Post-event timer (s) | S1 available ? | S2 available ? | Position | GenSet | Report EJP | Description | Post-event timer (s) | S1 available ? | S2 available ? | Position | GenSet | Report EJP
4500 | Yes | Basic in M/G: loss of S1, check that StartGen becomes ON and then that the product goes to P2 | Auto | 1P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | Yes | No | 1 | No check | OFF | (1) Turn off Source 1 | 6 | No | No | 1 | ON | OFF | (4) Turn on Source 2 | 5 | No | Yes | 2 | ON | OFF
4501 | Yes | Test come back in P1 when S1 returns | Auto | 1P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | No | Yes | 2 | ON | OFF | (3) Turn on Source 1 | 6 | Yes | Yes | 1 | ON | OFF | (0) No event | 125 | Yes | Yes | 1 | ON | OFF
4502 | Yes | Product is in P1, and recieve preavis EJP. Wait 20 min until StartGen becomes ON and switches to P2 | Auto | 1P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | Yes | No | 1 | No check | OFF | (17) Toggle preavis EJP input state | 5 | Yes | No | 1 | OFF | OFF | (0) No event | 1205 | Yes | No | 1 | ON | ON | (4) Turn on Source 2 | 8 | Yes | Yes | 2 | ON | ON
4503 | Yes | Product is in P2 because EJP is already active, preavis EJP ends : wait 10 min until product switches again to P1 and StartGen becomes OFF | Auto | 1P+N | UTIL | (O) Auto retransfer | (C) Preavis EJP ON | (O) Top EJP OFF | No | 0 | 0 | Yes | Yes | 2 | ON | ON | (17) Toggle preavis EJP input state | 605 | Yes | Yes | 1 | ON | OFF | (0) No event | 120 | Yes | Yes | 1 | OFF | OFF
4504 | Yes | Product is in P1, and recieve top EJP, check that StartGen becomes directly ON and product switches to P2 | Auto | 1P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | Yes | No | 1 | No check | OFF | (18) Toggle top EJP input state | 5 | Yes | No | 1 | ON | ON | (4) Turn on Source 2 | 8 | Yes | Yes | 2 | ON | ON
4505 | Yes | Product is in P2 because EJP is already active, top EJP ends : wait 10 min until product switches again to P1 and StartGen becomes OFF | Auto | 1P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (C) Top EJP ON | No | 0 | 0 | Yes | Yes | 2 | ON | ON | (18) Toggle top EJP input state | 605 | Yes | Yes | 1 | ON | OFF | (0) No event | 120 | Yes | Yes | 1 | OFF | OFF
4506 | Yes | Test return in P1 when S1 comes back and cooldown timer to stop StartGen | Auto | 1P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | No | Yes | 2 | ON | OFF | (3) Turn on Source 1 | 6 | Yes | Yes | 1 | ON | OFF | (0) No event | 125 | Yes | Yes | 1 | OFF | OFF
4507 | Yes | Idem case 4006 but auto retransfer is disabled, so the product stays in P2 after S1 return | Auto | 1P+N | UTIL | (C) Manual retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | No | Yes | 2 | ON | OFF | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | ON | OFF
4508 | Yes | Product is in P2 because EJP is already active, top EJP ends but auto retransfer is disabled : wait 10 min to check if product stays in P2 | Auto | 1P+N | UTIL | (C) Manual retransfer | (O) Preavis EJP OFF | (C) Top EJP ON | No | 0 | 0 | Yes | Yes | 2 | ON | ON | (18) Toggle top EJP input state | 605 | Yes | Yes | 2 | ON | OFF
4509 | Yes | Product is in P2 because EJP is already active with both S1 and S2 available, then S2 is lost so product must switch to P1 | Auto | 1P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (C) Top EJP ON | No | 0 | 0 | Yes | Yes | 2 | ON | ON | (2) Turn off Source 2 | 8 | Yes | No | 1 | ON | ON
4510 | Yes | Test fail timer : loss of S1, check that StartGen becomes ON after 20s | Auto | 1P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 20 | Yes | No | 1 | OFF | OFF | (1) Turn off Source 1 | 25 | No | No | 1 | ON | OFF
4511 | Yes | Test return timer: product is in P2 because S1 is not available, then S1 comes back so wait 10 min until product switches again to P1 | Auto | 1P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 600 | 0 | No | Yes | 2 | ON | OFF | (3) Turn on Source 1 | 605 | Yes | Yes | 1 | ON | OFF
4600 | No | Test EJP mode : top EJP recieved with only S1 available, no S2 start | Auto | 1P+N | EJP | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | Yes | No | 1 | OFF | OFF | (18) Toggle top EJP input state | 5 | Yes | No | 1 | ON | ON | (0) No event | 6 | Yes | No | 1 | ON | ON
4601 | No | Test EJP mode : EJP is already active, product is in P2, then S2 is lost but product doesn't switch to P1 | Auto | 1P+N | EJP | (O) Auto retransfer | (O) Preavis EJP OFF | (C) Top EJP ON | No | 0 | 0 | Yes | Yes | 2 | ON | ON | (2) Turn off Source 2 | 5 | Yes | No | 2 | ON | ON
4812 | No | Product in manual mode, in P1 with only S1 available, then S1 is lost but product doesn't switch to P2 | Manual | 1P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | Yes | No | 1 | No check | OFF | (1) Turn off Source 1 | 15 | No | No | 1 | No check | OFF
4822 | No | Product in manual mode, in P1 with both S1 and S2 available, then S2 is lost | Manual | 1P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | Yes | Yes | 1 | No check | OFF | (2) Turn off Source 2 | 6 | Yes | No | 1 | No check | OFF
4832 | No | No source available, product in P1 and manual mode. Then S1 comes back | Manual | 1P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | No | No | 1 | No check | OFF | (3) Turn on Source 1 | 8 | Yes | No | 1 | No check | OFF
4842 | No | No source available, product in P1 and manual mode. Then S2 comes back but product doesn't switch to P2 | Manual | 1P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | No | No | 1 | No check | OFF | (4) Turn on Source 2 | 8 | No | Yes | 1 | No check | OFF
4852 | No | No source available, product in P0 and manual mode. Then S1 comes back but product doesn't switch to P1 | Manual | 1P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | No | No | 0 | No check | OFF | (3) Turn on Source 1 | 8 | Yes | No | 0 | No check | OFF
4862 | No | No source available, product in P0 and manual mode. Then S2 comes back but product doesn't switch to P2 | Manual | 1P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | No | No | 0 | No check | OFF | (4) Turn on Source 2 | 8 | No | Yes | 0 | No check | OFF
4872 | No | No source available, product in P2 and manual mode. Then S1 comes back but product doesn't switch to P1 | Manual | 1P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | No | No | 2 | No check | OFF | (3) Turn on Source 1 | 8 | Yes | No | 2 | No check | OFF
4882 | No | No source available, product in P2 and manual mode. Then S2 comes back | Manual | 1P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | No | No | 2 | No check | OFF | (4) Turn on Source 2 | 8 | No | Yes | 2 | No check | OFF
4892 | No | Loss of S1, check that StartGen becomes ON but then open front control panel : the product doesn't switch to P2 | Auto | 1P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | Yes | No | 1 | No check | OFF | (1) Turn off Source 1 | 6 | No | No | 1 | ON | OFF | (12) Manually open front control panel | 5 | No | Yes | 1 | ON | OFF | (4) Turn on Source 2 | 8 | No | Yes | 1 | ON | OFF
4902 | No | Product in manual mode, send top EJP input but StartGen must stays OFF | Manual | 1P+N | UTIL | (O) Auto retransfer | (O) Preavis EJP OFF | (O) Top EJP OFF | No | 0 | 0 | Yes | No | 1 | OFF | OFF | (18) Toggle top EJP input state | 6 | Yes | No | 1 | OFF | OFF | (4) Turn on Source 2 | 15 | Yes | No | 1 | OFF | OFF

## ATYS_a_M0
|  |  | Config | [10 empty] | Initial state |  |  |  |  | Event1 |  | State1 |  |  |  |  | Event2 |  | State2 |  |  |  |  | Event3 |  | State3
Test case | Enable ? | Comments or test case description | Mode | Network | Network Application | InputFct1 | InputFct2 | InputFct3 | InputFct4 | Stop in 0 ? | RT (s) | FT (s) | CT (s) | S1 available ? | S2 available ? | Position | GenSet | Product Availability | Description | Post-event timer (s) | S1 available ? | S2 available ? | Position | GenSet | Product Availability | Description | Post-event timer (s) | S1 available ? | S2 available ? | Position | GenSet | Product Availability | Description | Post-event timer (s) | S1 available ? | S2 available ? | Position | GenSet | Product Availability
5000 | No | Basic in M/M: loss of S1, check that the product goes to P2, and back to P1 when S1 is recovered | Auto | 3P+N | M/M | (O) Fire input OFF | (O) Prio Source 1 | (O) Auto retransfer | (O) Inhibit signal OFF | No | 2 | 2 | 180 | Yes | Yes | 1 | No check | ON | (1) Turn off Source 1 | 6 | No | Yes | 2 | No check | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 1 | No check | ON
5001 | No | Basic in M/M: loss of one phase of S1, check that the product goes to P2, and back to P1 when S1 is recovered | Auto | 3P+N | M/M | (O) Fire input OFF | (O) Prio Source 1 | (O) Auto retransfer | (O) Inhibit signal OFF | No | 2 | 2 | 180 | Yes | Yes | 1 | No check | ON | (5) Lose one phase of Source 1 | 6 | Yes | Yes | 2 | No check | ON | (4) Turn on Source 2 | 6 | Yes | Yes | 2 | No check | ON
5002 | No | Manual retransfer selector test, check product stays in P2 after S1 is back until manual retransfer selector back to AUTO | Auto | 3P+N | M/M | (O) Fire input OFF | (O) Prio Source 1 | (C) Manual retransfer | (O) Inhibit signal OFF | No | 2 | 2 | 180 | Yes | Yes | 1 | No check | ON | (1) Turn off Source 1 | 6 | No | Yes | 2 | No check | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | No check | ON | (7) Toggle state of retransfer option | 6 | Yes | Yes | 1 | No check | ON
5003 | No | Manual retransfer selector test with a loss of S2 - check product stays in P2 after S1 is back, returns in P1 with a loss of S2 | Auto | 3P+N | M/M | (O) Fire input OFF | (O) Prio Source 1 | (C) Manual retransfer | (O) Inhibit signal OFF | No | 2 | 2 | 180 | Yes | Yes | 1 | No check | ON | (1) Turn off Source 1 | 6 | No | Yes | 2 | No check | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | No check | ON | (2) Turn off Source 2 | 6 | Yes | No | 1 | No check | ON
5004 | No | Priority input test (both sources available) then normal source loss sequence | Auto | 3P+N | M/M | (O) Fire input OFF | (O) Prio Source 1 | (O) Auto retransfer | (O) Inhibit signal OFF | No | 2 | 2 | 180 | Yes | Yes | 1 | No check | ON | (10) Toggle priority source | 6 | Yes | Yes | 2 | No check | ON | (2) Turn off Source 2 | 6 | Yes | No | 1 | No check | ON | (4) Turn on Source 2 | 6 | Yes | Yes | 2 | No check | ON
5005 | No | Prio S2, loss of S1 then PRIO S1 (nothing happens), move to S1 when S1 is back. | Auto | 3P+N | M/M | (O) Fire input OFF | (C) Prio Source 2 | (O) Auto retransfer | (O) Inhibit signal OFF | No | 2 | 2 | 180 | Yes | Yes | 2 | No check | ON | (1) Turn off Source 1 | 6 | No | Yes | 2 | No check | ON | (10) Toggle priority source | 6 | No | Yes | 2 | No check | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 1 | No check | ON
5006 | No | Fire input test (normal case, both source available) | Auto | 3P+N | M/M | (O) Fire input OFF | (O) Prio Source 1 | (O) Auto retransfer | (O) Inhibit signal OFF | No | 2 | 2 | 180 | Yes | Yes | 1 | No check | ON | (19) Toggle state of fire signal option | 6 | Yes | Yes | 0 | No check | OFF | (19) Toggle state of fire signal option | 6 | Yes | Yes | 1 | No check | ON
5007 | No | Fire input with opposite source not available, product is not inhibited, we wait until opposite source is present to put the product in 0. | Auto | 3P+N | M/M | (O) Fire input OFF | (O) Prio Source 1 | (O) Auto retransfer | (O) Inhibit signal OFF | No | 2 | 2 | 180 | Yes | No | 1 | No check | ON | (19) Toggle state of fire signal option | 6 | Yes | No | 1 | No check | OFF | (4) Turn on Source 2 | 6 | Yes | Yes | 0 | No check | OFF | (19) Toggle state of fire signal option | 6 | Yes | Yes | 1 | No check | ON
5008 | No | Fire input test with loss of prio source during FIRE active | Auto | 3P+N | M/M | (O) Fire input OFF | (O) Prio Source 1 | (O) Auto retransfer | (O) Inhibit signal OFF | No | 2 | 2 | 180 | Yes | Yes | 1 | No check | ON | (19) Toggle state of fire signal option | 6 | Yes | Yes | 0 | No check | OFF | (1) Turn off Source 1 | 6 | No | Yes | 0 | No check | OFF | (19) Toggle state of fire signal option | 6 | No | Yes | 2 | No check | ON
5009 | No | S1 is lost, INHIBIT signal test, get back S1, nothing happens until inhibit is removed | Auto | 3P+N | M/M | (O) Fire input OFF | (O) Prio Source 1 | (O) Auto retransfer | (O) Inhibit signal OFF | No | 2 | 2 | 180 | no | Yes | 2 | No check | ON | (8) Toggle state of inhibit auto option | 6 | No | Yes | 2 | No check | OFF | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | No check | OFF | (8) Toggle state of inhibit auto option | 6 | Yes | Yes | 1 | No check | ON
5010 | No | INHIBIT input active, loss of S1, only goes to P2 when inhibit is removed. | Auto | 3P+N | M/M | (O) Fire input OFF | (O) Prio Source 1 | (O) Auto retransfer | (C) Inhibit signal ON | No | 2 | 2 | 180 | Yes | Yes | 1 | No check | OFF | (1) Turn off Source 1 | 6 | No | Yes | 1 | No check | OFF | (8) Toggle state of inhibit auto option | 6 | No | Yes | 2 | No check | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 1 | No check | ON
5030 | No | Basic in M/M: loss of neutral from S1 only, check that the product goes to P2, and back to P1 when neutral is recovered | Auto | 3P+N | M/M | (O) Fire input OFF | (O) Prio Source 1 | (O) Auto retransfer | (O) Inhibit signal OFF | No | 2 | 2 | 180 | Yes | Yes | 1 | No check | ON | (20) Lose neutral of Source 1 | 6 | No | Yes | 2 | No check | ON | (21) Recover neutral of Source 1 | 6 | Yes | Yes | 1 | No check | ON
5031 | No | Basic in M/M 3P network: loss of S1, check that the product goes to P2, and back to P1 when S1 is recovered | Auto | 3P | M/M | (O) Fire input OFF | (O) Prio Source 1 | (O) Auto retransfer | (O) Inhibit signal OFF | No | 2 | 2 | 180 | Yes | Yes | 1 | No check | ON | (1) Turn off Source 1 | 6 | No | Yes | 2 | No check | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 1 | No check | ON
5011 | Yes | Basic in M/G: loss of S1, check genset start than the product goes to P2 | Auto | 3P+N | M/G | (O) Stop test | (O) Prio Source 1 | (O) Auto retransfer | (O) Inhibit signal OFF | No | 2 | 2 | 15 | Yes | No | 1 | OFF | ON | (1) Turn off Source 1 | 6 | No | No | 1 | ON | OFF | (4) Turn on Source 2 | 6 | No | Yes | 2 | ON | ON
5012 | Yes | S1 is back, check cooldown timer | Auto | 3P+N | M/G | (O) Stop test | (O) Prio Source 1 | (O) Auto retransfer | (O) Inhibit signal OFF | No | 2 | 2 | 15 | No | Yes | 2 | ON | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 1 | ON | ON | (0) No event | 20 | Yes | Yes | 1 | OFF | ON | (2) Turn off Source 2 | 6 | Yes | No | 1 | OFF | ON
5013 | Yes | Prio change M/G (set priority on the genset which is always on S2) | Auto | 3P+N | M/G | (O) Stop test | (O) Prio Source 1 | (O) Auto retransfer | (O) Inhibit signal OFF | No | 2 | 2 | 15 | Yes | No | 1 | OFF | ON | (10) Toggle priority source | 5 | Yes | No | 1 | ON | ON | (4) Turn on Source 2 | 6 | Yes | Yes | 2 | ON | ON
5014 | Yes | Prio on the genset, loss of S2, switch to P1 but genset signal stays ON | Auto | 3P+N | M/G | (O) Stop test | (C) Prio Source 2 | (O) Auto retransfer | (O) Inhibit signal OFF | No | 2 | 2 | 15 | Yes | Yes | 2 | ON | ON | (6) Lose one phase of Source 2 | 6 | Yes | Yes | 1 | ON | ON | (0) No event | 10 | Yes | Yes | 1 | ON | ON
5015 | Yes | Test on load start | Auto | 3P+N | M/G | (O) Stop test | (O) Prio Source 1 | (O) Auto retransfer | (O) Inhibit signal OFF | No | 2 | 2 | 15 | Yes | No | 1 | OFF | ON | (11) Toggle state of on load test option | 6 | Yes | No | 1 | ON | ON | (4) Turn on Source 2 | 6 | Yes | Yes | 2 | ON | ON
5016 | Yes | Test on load end | Auto | 3P+N | M/G | (C) Start test on load | (O) Prio Source 1 | (O) Auto retransfer | (O) Inhibit signal OFF | No | 2 | 2 | 15 | Yes | Yes | 2 | ON | ON | (11) Toggle state of on load test option | 8 | Yes | Yes | 1 | ON | ON | (0) No event | 20 | Yes | Yes | 1 | OFF | ON | (2) Turn off Source 2 | 6 | Yes | No | 1 | OFF | ON
5017 | Yes | Gen already available when loss S1, product goes directly to P2 | Auto | 3P+N | M/G | (O) Stop test | (O) Prio Source 1 | (O) Auto retransfer | (O) Inhibit signal OFF | No | 2 | 2 | 15 | Yes | Yes | 1 | No check | ON | (1) Turn off Source 1 | 6 | No | Yes | 2 | ON | ON
5018 | Yes | Loss of S2 during cooldown timer, genset is turned OFF | Auto | 3P+N | M/G | (O) Stop test | (O) Prio Source 1 | (O) Auto retransfer | (O) Inhibit signal OFF | No | 2 | 2 | 15 | No | Yes | 2 | ON | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 1 | ON | ON | (2) Turn off Source 2 | 6 | Yes | No | 1 | OFF | ON
5019 | Yes | Loss of S1, StartGen ON but S1 comes back : check StartGen shuts immediatly OFF and product is still in P1 | Auto | 3P+N | M/G | (O) Stop test | (O) Prio Source 1 | (O) Auto retransfer | (O) Inhibit signal OFF | No | 2 | 2 | 15 | Yes | No | 1 | No check | ON | (1) Turn off Source 1 | 6 | No | No | 1 | ON | OFF | (3) Turn on Source 1 | 8 | Yes | No | 1 | OFF | ON
5020 | Yes | Product in P2 with only S2 available, loss of S2 : check that product still in P2 but no more available | Auto | 3P+N | M/G | (O) Stop test | (O) Prio Source 1 | (O) Auto retransfer | (O) Inhibit signal OFF | No | 2 | 2 | 15 | No | Yes | 2 | ON | ON | (2) Turn off Source 2 | 6 | No | No | 2 | ON | OFF
5021 | Yes | Idem case 5020 but then S1 comes back : check product is available again but in P1 and StartGen OFF | Auto | 3P+N | M/G | (O) Stop test | (O) Prio Source 1 | (O) Auto retransfer | (O) Inhibit signal OFF | No | 2 | 2 | 15 | No | Yes | 2 | ON | ON | (2) Turn off Source 2 | 6 | No | No | 2 | ON | OFF | (3) Turn on Source 1 | 8 | Yes | No | 1 | OFF | ON
5022 | Yes | Product in P2 with only S2 available, manual retransfert mode, then S1 comes back but check that product stays in P2 | Auto | 3P+N | M/G | (O) Stop test | (O) Prio Source 1 | (C) Manual retransfer | (O) Inhibit signal OFF | No | 2 | 2 | 15 | no | Yes | 2 | ON | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | ON | ON | (7) Toggle state of retransfer option | 6 | Yes | Yes | 1 | ON | ON | (0) No event | 20 | Yes | No | 1 | OFF | ON
5023 | Yes | Manual retransfer selector test with a loss of S2 - check product stays in P2 after S1 is back, returns in P1 with a loss of S2 | Auto | 3P+N | M/G | (O) Stop test | (O) Prio Source 1 | (C) Manual retransfer | (O) Inhibit signal OFF | No | 2 | 2 | 15 | No | Yes | 2 | ON | ON | (3) Turn on Source 1 | 6 | Yes | Yes | 2 | ON | ON | (6) Lose one phase of Source 2 | 6 | Yes | Yes | 1 | ON | ON | (0) No event | 20 | Yes | Yes | 1 | OFF | ON
5024 | Yes | On genset, S1 dead, loss of S2 then S2 comes back : check product is available again in P2 | Auto | 3P+N | M/G | (O) Stop test | (O) Prio Source 1 | (O) Auto retransfer | (O) Inhibit signal OFF | No | 2 | 2 | 15 | No | Yes | 2 | ON | ON | (2) Turn off Source 2 | 6 | No | No | 2 | ON | OFF | (4) Turn on Source 2 | 8 | No | Yes | 2 | ON | ON
5025 | Yes | Inhibit while on S2, retrieve S1, enable again auto mode and check that the products switches to P1 | Auto | 3P+N | M/G | (O) Stop test | (O) Prio Source 1 | (O) Auto retransfer | (O) Inhibit signal OFF | No | 2 | 2 | 15 | No | Yes | 2 | ON | ON | (8) Toggle state of inhibit auto option | 6 | No | Yes | 2 | ON | OFF | (3) Turn on Source 1 | 8 | Yes | Yes | 2 | ON | OFF | (8) Toggle state of inhibit auto option | 20 | Yes | Yes | 1 | OFF | ON
5025 | Yes | Inhibit during load test | Auto | 3P+N | M/G | (O) Stop test | (O) Prio Source 1 | (O) Auto retransfer | (O) Inhibit signal OFF | No | 2 | 2 | 15 | Yes | Yes | 1 | No check | ON | (11) Toggle state of on load test option | 15 | Yes | Yes | 2 | ON | ON | (8) Toggle state of inhibit auto option | 6 | Yes | Yes | 2 | ON | OFF | (11) Toggle state of on load test option | 6 | Yes | Yes | 2 | ON | OFF
5026 | Yes | Check dynamic return timer (1RT = 20s, loose one phase of S2 before end of 1RT, if 3s are elapsed, switch back is done directly) | Auto | 3P+N | M/G | (O) Stop test | (O) Prio Source 1 | (O) Auto retransfer | (O) Inhibit signal OFF | No | 20 | 2 | 15 | No | Yes | 2 | ON | ON | (2) Turn off Source 2 | 6 | No | No | 2 | ON | OFF

## Datas_lists
Auto/Manual | Network | Network Application | InputFct1 | InputFct2 | InputFct3 | InputFct4 | Stop in 0 ? | EJP mode | RT (s) | FT (s) - tM | FT (s) | S available ? | Position | GenSet | Product Availability | Events gM tri | Events gM mono | Events tM | Events aM | Events gM SDMO tri | Events gM SDMO mono | Events aM0 | Enable
Auto | 3P+N | M/M | (O) Priority enabled | (O) Prio Source 1 | (O) Auto | (O) Inhibit signal OFF | Yes | UTIL | 0 | 0 | 0 | Yes | 0 | ON | ON | (0) No event | (0) No event | (0) No event | (0) No event | (0) No event | (0) No event | (0) No event | Yes
Manual | 1P+N | M/G | (C) Priority disabled | (C) Prio Source 2 | (C) Inhibit Auto | (C) Inhibit signal ON | No | EJP | 180 | 3 | 5 | No | 1 | OFF | OFF | (1) Turn off Source 1 | (1) Turn off Source 1 | (1) Turn off Source 1 | (1) Turn off Source 1 | (1) Turn off Source 1 | (1) Turn off Source 1 | (1) Turn off Source 1 | No
| 3P |  | (O) Auto retransfer | (O) Stop test | (O) Top EJP OFF |  |  |  | 600 | 10 | 20 |  | 2 | No check | No check | (2) Turn off Source 2 | (2) Turn off Source 2 | (2) Turn off Source 2 | (2) Turn off Source 2 | (2) Turn off Source 2 | (2) Turn off Source 2 | (2) Turn off Source 2
|  |  | (C) Manual retransfer | (C) Start test on load | (C) Top EJP ON |  |  |  | 1800 | 30 | 60 |  |  |  |  | (3) Turn on Source 1 | (3) Turn on Source 1 | (3) Turn on Source 1 | (3) Turn on Source 1 | (3) Turn on Source 1 | (3) Turn on Source 1 | (3) Turn on Source 1
|  |  | (O) Go to 0 disabled | (O) Preavis EJP OFF | (O) Auto retransfer | [9 empty] | (4) Turn on Source 2 | (4) Turn on Source 2 | (4) Turn on Source 2 | (4) Turn on Source 2 | (4) Turn on Source 2 | (4) Turn on Source 2 | (4) Turn on Source 2 | (4) Turn on Source 2
|  |  | (C) Go to 0 enabled | (C) Preavis EJP ON | (C) Manual retransfer | [9 empty] | (5) Lose one phase of Source 1 | (7) Toggle state of retransfer option | (5) Lose one phase of Source 1 | (5) Lose one phase of Source 1 | (5) Lose one phase of Source 1 | (7) Toggle state of retransfer option | (5) Lose one phase of Source 1 | (5) Lose one phase of Source 1
|  |  | (O) Stop test | (O) Default | [10 empty] | (6) Lose one phase of Source 2 | (8) Toggle state of inhibit auto option | (6) Lose one phase of Source 2 | (6) Lose one phase of Source 2 | (6) Lose one phase of Source 2 | (12) Manually open front control panel | (6) Lose one phase of Source 2 | (6) Lose one phase of Source 2
|  |  | (C) Start test on load | [11 empty] | (7) Toggle state of retransfer option | (9) Toggle state of priority enable option | (8) Toggle state of inhibit auto option | (8) Toggle state of inhibit auto option | (7) Toggle state of retransfer option | (13) Manually close front control panel | (7) Toggle state of retransfer option | (7) Toggle state of retransfer option
|  |  | (O) Fire input OFF | [11 empty] | (8) Toggle state of inhibit auto option | (10) Toggle priority source | (10) Toggle priority source | (12) Manually open front control panel | (12) Manually open front control panel | (14) Rapid toggle of Source 1 state 5x | (8) Toggle state of inhibit auto option | (8) Toggle state of inhibit auto option
|  |  | (C) Fire input ON | [11 empty] | (9) Toggle state of priority enable option | (11) Toggle state of on load test option | (12) Manually open front control panel | (13) Manually close front control panel | (13) Manually close front control panel | (17) Toggle preavis EJP input state | (10) Toggle priority source | (10) Toggle priority source
[15 empty] | (10) Toggle priority source | (12) Manually open front control panel | (13) Manually close front control panel | (14) Rapid toggle of Source 1 state 5x | (14) Rapid toggle of Source 1 state 5x | (18) Toggle top EJP input state | (11) Toggle state of on load test option | (11) Toggle state of on load test option
[15 empty] | (11) Toggle state of on load test option | (13) Manually close front control panel | (14) Rapid toggle of Source 1 state 5x | (15) Toggle state of go to position 0 option | (17) Toggle preavis EJP input state |  | (12) Manually open front control panel | (12) Manually open front control panel
[15 empty] | (12) Manually open front control panel | (14) Rapid toggle of Source 1 state 5x | (15) Toggle state of go to position 0 option | (16) Double toggle of inhibit auto option | (18) Toggle top EJP input state |  | (13) Manually close front control panel | (13) Manually close front control panel
[15 empty] | (13) Manually close front control panel |  | (16) Double toggle of inhibit auto option |  |  |  | (19) Toggle state of fire signal option | (19) Toggle state of fire signal option
[15 empty] | (14) Rapid toggle of Source 1 state 5x | [6 empty] | (20) Lose neutral of Source 1
(21) Recover neutral of Source 1
Recover phase ? Ou alors Turn on Sx ?