SECTION 26 36 23

AUTOMATIC TRANSFER SWITCHING EQUIPMENT

PART 1 – GENERAL

  - SCOPE SUMMARY

- This section includes “Automatic Transfer Switching Equipment” (ATSE).

- All ATSE is to be designed as one integrated product (power switching, motorisation and ATS Control), shall be of the same recognised manufacturer and shall be tested to IEC 60947-6-1 as one complete automatic transfer switch.

  - SUBMITTALS

- Product data including: Rated operational voltage and current capacity, number of poles (fully rated) and characteristics according to IEC 60947-6-1 and IEC 60947-3.

- Metric dimensional drawings issued by the manufacturer for the complete ATSE including front, side and top views together with provision for power terminal connections.

- Instructions for back plate and flush mounting installation of the ATSE within an enclosure.

- Instruction manual specific to the ATSE, published in the English language by the manufacturer.

- Quick Start Instruction sheet specific to the ATSE and published by the manufacturer.

- Quality control test reports issued by the manufacturer for the ATSE.

- A certificate issued by the manufacturer to certify that the ATSE supplied is in full compliance with the requirements included in this specification.

  - STANDARDS AND QUALITY ASSURANCE

- The ATSE supplied must comply with Class PC of IEC 60947-6-1: (Low-voltage switchgear and control gear - Multiple function equipment – Transfer switching equipment).

- Besides IEC 60947-6-1 the ATSE supplied must also comply with IEC 60947-3: (Low-voltage switchgear and control gear – Switches, disconnectors, switch-disconnectors and fuse-combination units).

- The ATSE supplied is to be designed and built as a fully integrated product (power switching, motorisation and ATS Control), shall be of the same recognized manufacturer and shall be tested to IEC 60947-6-1 as one complete unit.

- The ATSE label shall include data markings and compliance to IEC 60947-6-1 and IEC 60947-3.

- The manufacturer shall be certified ISO 9001: 2008 with third party certification verifying its Quality Assurance in design and production in accordance with ISO 9001.

PART 2 – PRODUCTS

  - ACCEPTABLE ATSE and MANUFACTURERS

- The ATSE shall be in full compliance with this specification and will be one of the following :

  - SOCOMEC “ATyS p M ”.

  - …..

  - GENERAL CONSTRUCTION

- The ATSE shall be composed of :

  - An open transition break before make architecture (I – 0 – II), in full compliance with IEC 60947-6-1 Class PC.

  - Two side-by-side, fully rated, IEC 60947-3 compliant, load break switch disconnects.

  - A maintenance free switch design that includes self-cleaning contacts on all poles.

  - An inherent fully integrated robust mechanical interlock between both switches.

  - An independent switching mechanism free from external factors during transfer.

  - A wide band (control voltage of 50/60Hz, 161-299Vac) electronic control fit directly to the switching mechanism.

  - An integrated ATS controller with dual power supply (DPS) and 3 phase sensing on both source supplies.

  - Dual emergency manual operation.

  - Padlocking in the zero position with the use of up to 3x 8mm padlocks.

  - Clear switch position indication (I – 0 – II).

- The ATSE shall be fully integrated in one device:

Besides customer I/O, no additional wiring between functional units other than the power connections shall be necessary to allow the proper functioning of the ATSE.

- The ATSE should include a programmable “Product Available Output”. The product should analyse / test its condition periodically and communicate through dry contacts to report the ability of the transfer switching equipment to operate.

  - RATINGS AND ATSE TEST

- Characteristics, nominal phase voltage, current ratings, number of poles and withstand ratings shall be as shown on the drawings. The ampere ratings shall be for 100% continuous load current with the neutral pole fully rated.

- Ratings and characteristics shall be according to IEC 60947-6-1 and IEC 60947-3 with non-welding of contacts during the performance of withstand and closing tests.

- The complete ATSE shall be fully factory assembled by the manufacturer and tested to IEC 60947-6-1 so as to ensure proper operation of the ATSE as a complete system with a good overall operation sequence. The test must also ensure that the operating transfer time, voltage, frequency and time delay settings are in compliance with the specification requirements.

  - DESIGN REQUIREMENTS:

- The ATSE shall have 3 stables positions: I – 0 - II.

- Besides the ATSE features as per IEC 60947-6-1, the equipment shall be a Load Break and Disconnect switch as per IEC 60947-3 with padlocking with a minimum of one padlock only.

- The ATSE shall be of the clearly visible position indication type with markings I - 0 - II

- The ATSE shall be electrically operated and fully automatic with the possibility to override the automation and operate remotely via dry contact inputs for position orders.

- Emergency manual operation shall be provided using a handle.

- The ATSE shall be self-powered.

- The ATSE shall have a distinct manual / automatic mode selectable by opening a cover.

- The neutral pole of the ATSE switches shall be fully rated and configurable for left or right connection.

- The ATSE shall have no power consumption while in a stable position other than that required for the ATS control unit.

- The 4 poles shall switch simultaneously to avoid potential floating neutral issues during switching.

  - SAFETY REQUIREMENTS & FEATURES:

- Under no circumstance (including equipment failure) should it be possible to close switch I and switch II simultaneously.

- During manual operation, opening and closing of the contacts must be independent from the emergency handle operating speed.

- The ATSE shall have a built-in provision for padlocking in the O position. One x4mm padlock should be sufficient to padlock whilst it should be possible to use up to 3x 8mm padlocks.

- All operating modes shall be inhibited when the product is padlocked.

- Padlocking shall only be possible with the switch in manual position.

- An emergency handle shall be provided for manual operation.

- The ATSE should allow manual switching I-0-II at full load without damage to the contacts.

  - BASIC OPERATION:

- The ATSE should have distinct Auto and Manual operational modes that should be fully operational under any load condition. (Within the product ratings intended scope).

- The ATSE power section shall have a high short time withstand current capability. (Icw 1s)

- An automatic retransfer function should be included with the facility to inhibit retransfer locally or remotely through dry contacts.

- The ATSE shall have the facility to inhibit the ATS controller and electrically change the switch state to any position (I – 0 – II) through programmable inputs.

- Cable length for remote dry contact order inputs is to be ≤100m.

  - ATS CONTROLS

- The ATSE shall have a fully integrated ATS Controller.

- The controller shall include an LCD display, LED’s and a keypad with front access.

- Electrical motorised control (position I, O, II) should be available locally through the keypad, remotely through dry contacts and optionally through communication.

- Main Parameters:

- The ATS controller shall include 3 phase and neutral sensing for the monitoring of voltage and frequency on both source supplies.

- Voltage settings shall be field adjustable in increments of 1%.

- Frequency settings shall be field adjustable in 0.1% increments.

- Setting configuration shall be adjustable through software (on versions with COM) as well as directly from the keypad on the front face.

- The ATS Controller shall have phase sequence detection and allow the user to choose the desired sequence (ACB or ABC).

- Automatic changeover shall be forbidden if the supply phase sequences are different.

- The ATS Controller shall have the possibility to select the network type.

- The ATS Controller shall allow the setting of the source priority.

- The ATS controller shall be able to measure phase unbalance.

  - ATSE INTERFACE:

- The ATS Controller is to be easily configurable via an HMI keypad directly on the controller, a remote control and display unit and via dedicated ATSE software (on version with COM).

- Status of the ATSE shall be clearly visible through LED’s on the front of the unit.

  - ATSE INPUTS & OUTPUTS, COMMUNICATION:

- The ATSE shall include a genset start relay.

- The ATSE shall be able to provide three programmable inputs and three programmable outputs.

  - COMMUNICATION

- The ATSE is to propose a version including RS 485 MODBUS Communication.

- It shall be possible to configure all the ATSE parameters via the dedicated simple configuration software tools.

- The settings file should allow to be saved on any external data storage media for a simple and quick download of multiple product configurations.

- Configuration software is to be available free on the manufacturer’s website.

- Configuration and control through software is to be password protected.

  - TIMER SETTINGS:

- Two adjustable timers of 0 to 60 seconds shall be provided to detect source 1 or source 2 failures, and to override any transient outages of the normal supply. (Source 1 Failure Timer, 1FT and Source 2 Failure Timer, 2FT).

- A timer of 0 to 3600 seconds shall be provided for source 2 available so as to ensure stability of the alternative network before transfer. (Source 2 Available Timer, 2AT).

- A possibility to stay in switch position I or II shall be provided with an adjustment of 0 to 10 seconds prior to return to the 0 position. (0 Timer, 1OT, 2OT). Only to be accessible with parameter RETURN to 0 activated.

- An adjustable timer of 0 to 3600 seconds shall be provided to detect priority network return to normal so as to override any incorrect availability of the normal supply. (Main Return Timer, 1RT, 2RT).

- An adjustable timer of 0 to 600 seconds shall be provided to allow the generator to cool down after the load retransfer from alternative back to the normal supply. (Cool Down Timer, 2CT accessible in Mains – Gen applications).

  - ON LOAD / OFF LOAD TESTS

- The ATSE should include for On-Load as well as Off-Load tests associated with Mains – Gen applications. (The test will as a minimum start the Genset for a determined period of time). These tests should be operable manually through the keypad, through remote inputs and through MODBUS communication (on versions with COM).

  - MAINTENANCE

- Once installed, the ATSE shall be “Maintenance Free” however it would be recommended to switch through at least one complete cycle once a year.

PART 3 – EXECUTION

3.01	INSTALLATION

- Preparation shall be in accordance with the reviewed product data, final shop drawings and the manufacturer’s recommendations.

- Installation shall be in accordance with manufacturer’s instructions and recommendations.

- Identify components according to Division 26 section “Identification for Electrical Systems”.

3.02	CONNECTION

- Wiring for the ATSE equipment shall be in accordance with manufacturer’s instructions.

- Connections and wiring shall be according to Division 26 section “low-Voltage Electrical Power Conductors and cables”.

3.03	MAINTENANCE & TRAINING

- Operational and Maintenance Instructions:  Personnel on site should be formally trained by the manufacturer’s authorised representative. This is with regards to the proper operation and maintenance of the automatic transfer switching equipment.

3.04	TESTING

- The ATSE shall be declared compliant to the IEC standards listed above by a testing laboratory having delegation or working under contract for certification to UL and IEC standards under the IEC Electrotechnical Equipment (IECEE) certification body scheme.

- After installation of the equipment, a test report is to be submitted to state that the equipment has been installed and commissioned in accordance with the manufacturer’s instructions.

END OF SECTION 26 36 23